## Capex
No | Items | System | Findings | Cause | Operated_by | Vendors | Area | Level | Zone | Facility | Discipline | YearBuilt | S | CO | SE | HE | R | Interventions | IS | Quantity | Unit | InterPer | Cost | Span | Probability | Year | Binary_highrisk | Binary_option | NPV | NPV_HighRisk | NPV_Option | Remarks | Drawing_reference | Picture_reference | Cost Reference
SMC-001 | 537 KVA Diesel Generator | Standby Generator System | 1) At least one major corrective intervention has been reported, however, the cause of the damage was not disclosed. 2.) 30% of the total power were only backed up. 3.) The generators of GMCAC will not operate if MCIA is operating their generator. However, only 1 of the 2 generators of MCIA is working, and can only supply 50% of the total load of airport during emergency. 4.) 'Still working however there is a risk of not providing adequate level of services due to low reliability because of aging. | Damage | GMCAC | Third Party | Terminal 1 | Arrival | Zone A2 | Generator Room | Electrical | 1994 | 4 | 3 | 4 | 3 | 3 | Renewal with bigger size of GENSET to cater the 100% load. | 6 | 2 | no | 1 | 13000000 |  | 1 | 0 | 1 | 0 | 0 | 26000000 | 0 |  |  |  | Cost Database
SMC-002 | 1500L Fuel Tank | Standby Generator System | 1.) Fuel Tank pumping is mannually operated. 2.) Fuel Tank monitoring is manual. 3.) At least one major corrective intervention has been reported, however, the cause of the damage was not disclosed. | Damage | GMCAC | Thirdy Party | Terminal 1 | Arrival | Zone A2 | Generator Room | Electrical | 1994 | 4 | 3 | 4 | 3 | 3 | Installation of sensors and gas leakage montironing devices. | 4 | 2 | no | 1 | 365000 |  | 1 | 0 | 1 | 0 | 0 | 730000 | 0 |  |  |  | Cost Database
SMC-003 | 2.5 MVA Dry-Type Transformer | Low Voltage Distribution | Still working however there is a risk of not providing adequate level of services due to low reliability because of aging. | Aging | GMCAC | Thirdy Party | Terminal 1 | Arrival | Zone A2 | Substation Room | Electrical | 1994 | 4 | 3 | 4 | 3 | 3 | Renewal of transformer | 6 | 2 | no | 1 | 4950000 |  | 1 | 0 | 1 | 0 | 0 | 9900000 | 0 |  |  |  | Cost Database
SMC-004 | 1 MVA Dry-Type Transformer | Low Voltage Distribution | Still provide adequate LOS and in good condition |  | GMCAC | Thirdy Party | Terminal 1 | Arrival | Zone A2 | Substation Room | Electrical | 2019 | 2 | 2 | 2 | 2 | 1 | Routine/regular maintennace | 4 | 1 | no | 1 | 0 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 |  |  |  | no cost; part of OPEX
SMC-005 | 0.5 MVA Dry-Type Transformer | Low Voltage Distribution | Still working however there is a risk of not providing adequate level of services due to low reliability because of aging. | Aging | GMCAC | Thirdy Party | Terminal 1 | Arrival | Zone A2 | Substation Room | Electrical | 1994 | 4 | 2 | 4 | 3 | 3 | Renewal of transformer | 6 | 3 | no | 1 | 2560000 |  | 1 | 0 | 1 | 0 | 0 | 7680000 | 0 |  |  |  | Cost Database
SMC-006 | 0.5 MVA Dry-Type Transformer | Low Voltage Distribution | Still provide adequate LOS and in good condition |  | GMCAC | Thirdy Party | Terminal 1 | Arrival | Zone A2 | Substation Room | Electrical | 2019 | 2 | 2 | 2 | 2 | 1 | preventive maintenance | 1 | 1 | no | 1 | 0 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 |  |  |  | no cost; part of OPEX
SMC-007 | 0.3 MVA Dry-Type Transformer | Low Voltage Distribution | Minor sign of outside deterioration is observed, mostly with the paint |  | GMCAC | Thirdy Party | Terminal 1 | Arrival | Zone A2 | Substation Room | Electrical | 2010 | 2 | 2 | 2 | 2 | 1 | preventive maintenance | 1 | 2 | no | 1 | 0 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 |  |  |  | no cost; part of OPEX
SMC-008 | 0.225 MVA Dry-Type Transformer | Low Voltage Distribution | Minor sign of outside deterioration is observed, mostly with the paint |  | GMCAC | Thirdy Party | Terminal 1 | Arrival | Zone A2 | Substation Room | Electrical | 2010 | 2 | 2 | 2 | 2 | 1 | preventive maintenance | 1 | 1 | no | 1 | 0 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 |  |  |  | no cost; part of OPEX
SMC-009 | 0.1 MVA Dry-Type Transformer | Low Voltage Distribution | Minor sign of outside deterioration is observed, mostly with the paint |  | GMCAC | Thirdy Party | Terminal 1 | Arrival | Zone A2 | Substation Room | Electrical | 2010 | 2 | 2 | 2 | 2 | 1 | preventive maintenance | 1 | 1 | no | 1 | 0 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 |  |  |  | no cost; part of OPEX
SMC-010 | Automatic Transfer Switch | Low Voltage Distribution | Minor sign of outside deterioration is observed, mostly with the paint |  | GMCAC | Thirdy Party | Terminal 1 | Arrival | Zone A2 | Substation Room | Electrical | 2010 | 2 | 2 | 2 | 2 | 1 | preventive maintenance | 1 | 1 | lot | 1 | 0 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 |  |  |  | no cost; part of OPEX
SMC-011 | Uninterruptible Power Supply | Low Voltage Distribution | 1.) The UPS has thermal issue. Airblasters are being used as alternative cooling equipment. 2.) UPS can provide emergency power to 100% of critical loads such as IT system and security control cameras. | Damage | GMCAC | Thirdy Party | Terminal 1 | Arrival | Zone C3 | UPS Room | Electrical | 2019 | 4 | 4 | 4 | 4 | 3 | Provision of HVAC system inside the UPS room. | 4 | 1 | lot | 1 | 1200000 |  | 1 | 0 | 1 | 0 | 0 | 1200000 | 0
SMC-012 | Uninterruptible Power Supply | Low Voltage Distribution | UPS may be affected with the prolonged lack of cooling. | Damage | GMCAC | Thirdy Party | Terminal 1 | Arrival | Zone C3 | UPS Room | Electrical | 2019 | 4 | 4 | 4 | 4 | 3 | Tests to be conducted on UPS to assess the damage caused by thermal issue. | 7 | 1 | lot | 0.05 | 5400000 |  | 1 | 0 | 1 | 0 | 0 | 270000 | 0
SMC-013 | Battery Charger | Low Voltage Distribution | Still provide adequate LOS and in good condition |  | GMCAC | Thirdy Party | Terminal 1 | Arrival | Zone C3 | UPS Room | Electrical | 2019 | 2 | 2 | 2 | 2 | 1 | preventive maintenance | 1 | 1 | lot | 1 | 0 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0 |  |  |  | no cost; part of OPEX
SMC-014 | Power Factor Correction | Low Voltage Distribution | Still working however there is a risk of not providing adequate level of services due to low reliability because of aging. | Aging | GMCAC | Thirdy Party | Terminal 1 | Arrival | Zone A2 | Substation Room | Electrical | 1994 | 4 | 4 | 4 | 3 | 3 | Renewal of Capacitor Banks | 6 | 1 | lot | 1 | 2100000 |  | 1 | 0 | 1 | 0 | 0 | 2100000 | 0 |  |  |  | Cost Database
SMC-015 | LV Switchboards | Low Voltage Distribution | 1.) Still working however there is a risk of not providing adequate level of services due to low reliability because of aging. 2.) Corrective Maintenance were also done on some parts of the switchboard. | Aging | GMCAC | Thirdy Party | Terminal 1 | Arrival | Zone A2 | Substation Room | Electrical | 1994 | 4 | 4 | 4 | 3 | 3 | Renewal of LV Switchboards | 6 | 1 | lot | 1 | 34000000 |  | 1 | 0 | 1 | 0 | 0 | 34000000 | 0 |  |  |  | Cost Database
SMC-016 | Electrical Feeder Cables | Low Voltage Distribution | 1.) 10% were damaged. 2.) There is a risk of not providing adequate level of services due to low reliability because of aging for remaining. | Typhoon Odette "Rai" | GMCAC | Thirdy Party | Airside | Apron | All Zone | General | Electrical | 1994 | 5 | 4 | 5 | 5 | 3 | Renewal of Electrical Feeder Cables | 6 | 1 | lot | 0.1 | 9700000 |  | 1 | 0 | 1 | 0 | 0 | 970000 | 0 |  |  |  | Cost Database
SMC-017 | Electrical Feeder Cables | Low Voltage Distribution | 1.) Still working however there is a risk of not providing adequate level of services due to low reliability because of aging. 2.) Some cables had undergone replacement during renovation in 2018. | Aging | GMCAC | Thirdy Party | Terminal 1 | Arrival | Zone A2 | Substation Room | Electrical | 1994 | 4 | 4 | 4 | 3 | 3 | Renewal of Electrical Feeder Cables | 6 | 1 | lot | 1 | 9700000 |  | 1 | 0 | 1 | 0 | 0 | 9700000 | 0 |  |  |  | Cost Database
SMC-018 | Busbars | Low Voltage Distribution | 1.) Still working however there is a risk of not providing adequate level of services due to low reliability because of aging. 2.) Preventive maintenance is performed annually. | Aging | GMCAC | Thirdy Party | Terminal 1 | Arrival | Zone A2 | Substation Room | Electrical | 1994 | 4 | 4 | 4 | 3 | 3 | Renewal of Electrical Busbars | 6 | 1 | lot | 1 | 20000000 |  | 1 | 0 | 1 | 0 | 0 | 20000000 | 0 |  |  |  | Cost Database
SMC-019 | Cable Trays | Low Voltage Distribution | 1.) Still working however there is a risk of not providing adequate level of services due to low reliability because of aging. | Aging | GMCAC | Thirdy Party | Terminal 1 | Arrival | Zone A2 | Substation Room | Electrical | 1994 | 4 | 4 | 4 | 3 | 3 | Renewal of Electrical Cable Trays | 6 | 1 | lot | 1 | 14500000 |  | 1 | 0 | 1 | 0 | 0 | 14500000 | 0 |  |  |  | Cost Database
SMC-020 | Normal Lighting | General Lighting and Power System | 1.) 5% of the normal lightings were already busted in North Wing Arrival. 2.) No spares for Lighting Bulbs & Fixtures. | Typhoon Odette "Rai" | GMCAC | Thirdy Party | Terminal 1 | Arrival | Zone B3 | General | Electrical | 2018 | 5 | 4 | 5 | 5 | 2 | Replacement of Normal Lightings | 5 | 1 | lot | 0.05 | 13778800 |  | 1 | 0 | 0 | 0 | 688940 | 0 | 0 |  |  |  | Cost Database
SMC-021 | Normal Lighting | General Lighting and Power System | 1.) 10% of the normal lightings were already busted. 2.) 50% of the lightings were not yet LED. 3.) No spares for Lighting Bulbs & Fixtures. | Damage | GMCAC | Thirdy Party | Terminal 1 | Departure | General | General | Electrical | 2018 | 5 | 4 | 5 | 5 | 2 | Replacement of Normal Lightings | 5 | 1 | lot | 0.2 | 13778800 |  | 1 | 0 | 0 | 0 | 2755760 | 0 | 0 |  |  |  | Cost Database
SMC-022 | Normal Lighting | General Lighting and Power System | 1.) 40% of the normal lightings were already busted. 2.) 50% of the lightings were not yet LED. 3.) No spares for Lighting Bulbs & Fixtures. | Damage | GMCAC | Thirdy Party | Terminal 1 | Arrival | General | General | Electrical | 2018 | 5 | 4 | 5 | 5 | 2 | Replacement of Normal Lightings | 5 | 1 | lot | 0.2 | 13778800 |  | 1 | 0 | 0 | 0 | 2755760 | 0 | 0 |  |  |  | Cost Database
SMC-023 | Emergency Exit Lights | General Lighting and Power System | 1.)Generally, the emergency lights were not working. | Typhoon Odette "Rai" | GMCAC | Thirdy Party | Terminal 1 | General | General | General | Electrical | 2018 | 5 | 4 | 5 | 5 | 2 | Replacement of Emergency Exit Lightings | 5 | 1 | lot | 0.3 | 2600000 |  | 1 | 0 | 0 | 0 | 780000 | 0 | 0 |  |  |  | Cost Database
SMC-024 | Directional Signages | General Lighting and Power System | 1.) 90% of the directional signages were damaged. | Typhoon Odette "Rai" | GMCAC | Thirdy Party | Terminal 1 | Arrival | General | General | Electrical | 2018 | 5 | 4 | 5 | 5 | 2 | Replacement of directional signages | 5 | 1 | lot | 1 | 2130000 |  | 1 | 0 | 0 | 0 | 2130000 | 0 | 0 |  |  |  | Cost Database
SMC-025 | Carpark Lighting | General Lighting and Power System | 1.) 2-3% of the carpark lighting were damaged. 2.) No spares for Lighting Bulbs & Fixtures. | Typhoon Odette "Rai" | GMCAC | Thirdy Party | Terminal 1 | Arrival | General | General | Electrical | 2010 | 5 | 4 | 5 | 5 | 2 | Replacement of damaged carpark lighting | 5 | 1 | lot | 1 | 1359375 |  | 1 | 0 | 0 | 0 | 1359375 | 0 | 0 |  |  |  | Cost Database
SMC-026 | High Mast Lighting | General Lighting and Power System | 1.) Power supply for 3 fixed pole were damaged. 2.) 6 out of 14 poles had defective lightings. 3.) Controls for High Mast Lighting are manual since BMS is not existing on Terminal 1. | Typhoon Odette "Rai" | GMCAC | Thirdy Party | Terminal 1 | Apron | General | General | Electrical | 2010 | 5 | 4 | 5 | 5 | 2 | Replacement of damaged high mast lights Automation of Monitoring and Control for High Mast Lighting | 5 | 1 | lot | 0.6 | 15312500 |  | 1 | 0 | 0 | 0 | 9187500 | 0 | 0 |  |  |  | Cost Database (8 floodlights per pole)
SMC-027 | Obstruction Lights | General Lighting and Power System | 1.) Obstruction lights are in good condition. |  | GMCAC | Thirdy Party | Terminal 1 | Apron | General | General | Electrical | 2010 | 2 | 2 | 2 | 2 | 1 | preventive maintenance | 1 | 1 | lot | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | no cost; part of OPEX
SMC-028 | Airfield Ground Lighting (by MCIA) | General Lighting and Power System | 1.) High possibility of damaged / busted Airfield Ground Lights on runway due to Typhoon Odette. 2.) Still working however there is a risk of not providing adequate level of services due to low reliability because of aging. | Typhoon Odette "Rai" | MCIAA | Thirdy Party | Airside | Apron | General | General | Electrical | 1994 | 4 | 4 | 3 | 3 | 3 | replacement of airfield ground lighting | 5 | 1 | lot | 0.3 | 13250000 |  | 1 | 0 | 0 | 0 | 3975000 | 0 | 0 |  |  |  | market rate
SMC-029 | Approach Lighting (by MCIA) | General Lighting and Power System | 1.) 15% of the Approach Lighting were damaged. 2.) Still working however there is a risk of not providing adequate level of services due to low reliability because of aging. | Typhoon Odette "Rai" | MCIAA | Thirdy Party | Airside | Apron | General | General | Electrical | 1994 | 4 | 4 | 3 | 3 | 3 | replacement of approach lighting | 5 | 1 | lot | 0.15 | 4875000 |  | 1 | 0 | 0 | 0 | 731250 | 0 | 0 |  |  |  | market rate (5 approach light per pole, total of 13 poles)
SMC-030 | Outlets | General Lighting and Power System | 1.) minor deterioration or damaged on covers of power outlets. | Damage | GMCAC | Thirdy Party | Terminal 1 | General | General | General | Electrical | 2010 | 3 | 3 | 3 | 4 | 2 | corrective interventon of small power outlets | 2 | 1 | lot | 0.5 | 995000 |  | 1 | 0 | 0 | 0 | 497500 | 0 | 0 |  |  |  | Cost Database
SMC-031 | General Lighting and Power Roughing - Ins and accessories | General Lighting and Power System | 1.) 90% of the junction box were already corroded. 2.) Roughing - Ins tagging were not found on some areas. | Damage | GMCAC | Thirdy Party | Terminal 1 | General | General | General | Electrical | 2010 | 4 | 4 | 4 | 4 | 3 | corrective interventon of general lighting and power roughing - ins and accessories | 2 | 1 | lot | 0.9 | 505000 |  | 1 | 0 | 0 | 0 | 454500 | 0 | 0 |  |  |  | Cost Database
SMC-032 | Earthing and Lightning Devices | Earthing and Lightning System | 1.) Still working however there is a risk of not providing adequate level of services due to low reliability because of aging. 2.) Earth Bars and Grounding System are in good condition. Annual preventive maintenance is conducted. | Aging | GMCAC | Thirdy Party | Terminal 1 | Arrival | Zone A2 | Substation Room | Electrical | 1994 | 4 | 4 | 4 | 4 | 3 | Renewal of earthing and lightning devices | 6 | 1 | lot | 1 | 4422400 |  | 1 | 0 | 0 | 0 | 4422400 | 0 | 0 |  |  |  | Cost Database
SMC-033 | Solar Panels | Photovoltaic System | 1.) 93 out of 17,000 panels were damaged by the typhoon | Typhoon Odette "Rai" | GMCAC | Thirdy Party | Terminal 1 | Roof Level | General | General | Electrical | 2018 | 4 | 4 | 4 | 4 | 3 | replacement of damaged solar panels | 5 | 1 | lot | 0.1 | 45000000 |  | 1 | 0 | 0 | 0 | 4500000 | 0 | 0 |  |  |  | Cost Database, percentage loading
SMC-034 | Electrical Feeder Cables | Low Voltage Distribution | 1.) The feeder cables were not fully loaded. Has provision for expansion. 2.) The feeder cables have tagging. |  | GMCAC | Thirdy Party | Terminal 2 | Arrival | Zone E1 | Substation Room | Electrical | 2018 | 2 | 2 | 2 | 2 | 1 | Routine/regular maintennace | 1 | 1 | lot | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | no cost; part of OPEX
SMC-035 | Power Factor Correction | Low Voltage Distribution | 1.) The power factor correction are in good condition. 2.) Annual Preventive Maintenance is conducted. |  | GMCAC | Thirdy Party | Terminal 2 | Arrival | Zone E1 | Substation Room | Electrical | 2018 | 2 | 2 | 2 | 2 | 1 | preventive maintenance | 1 | 1 | lot | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | no cost; part of OPEX
SMC-036 | Low Voltage Switchboard | Low Voltage Distribution | 1.) The Swtichboards are in good condition. 2.) Spares and Spaces were found on switchboard. |  | GMCAC | Thirdy Party | Terminal 2 | Arrival | Zone E1 | Substation Room | Electrical | 2018 | 2 | 2 | 2 | 2 | 1 | preventive maintenance | 1 | 1 | lot | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | no cost; part of OPEX
SMC-037 | 2.5MVA Dry-Type Transformer | Low Voltage Distribution | 1.) The Transformers are still in good condition. 2.) Annual Preventive Maintenance is conducted. |  | GMCAC | Thirdy Party | Terminal 2 | Arrival | Zone E1 | Substation Room | Electrical | 2018 | 2 | 2 | 2 | 2 | 1 | preventive maintenance | 1 | 3 | no | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | no cost; part of OPEX
SMC-038 | 1.5MVA Diesel Generator | Standby Generator System | 1.) 2 out of 3 Diesel Generator had corrective maintenance due to damages caused by Typhoon Odette. 2.) The Diesel Generator can provide emergency power for 100% load. 3.) Has provision of 1.5MVA for future expansion. 4.) Louver to be upgraded on Genset Room |  | GMCAC | Thirdy Party | Terminal 2 | Apron | Zone E1 | Generator Room | Electrical | 2018 | 2 | 2 | 2 | 2 | 1 | preventive maintenance and monitoring | 1 | 3 | no | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | no cost; part of OPEX
SMC-039 | 1000L Day Tank | Standby Generator System | 1.) The day tank is still on good condition 2.) The monitoring of fuel level is automated. 3.) The refilling of fuel is automated. |  | GMCAC | Thirdy Party | Terminal 2 | Apron | Zone E1 | Generator Room | Electrical | 2018 | 2 | 2 | 2 | 2 | 1 | preventive maintenance | 1 | 3 | no | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | no cost; part of OPEX
SMC-040 | 15,000 Mother Tank | Standby Generator System | 1.) The mother tank is still on good condition 2.) The monitoring of fuel level is automated. 3.) The refilling of fuel is automated. |  | GMCAC | Thirdy Party | Terminal 2 | Apron | Zone E1 | Generator Room | Electrical | 2018 | 2 | 2 | 2 | 2 | 1 | preventive maintenance | 1 | 1 | no | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | no cost; part of OPEX
SMC-041 | Carpark Lighting | General Lighting and Power System | 1.) 30% of carpark Lightings were damaged. 2.) No provions/spare for Lighting Fixtures | Typhoon Odette "Rai" | GMCAC | Thirdy Party | Terminal 2 | Arrival | All Zone | General | Electrical | 2018 | 4 | 4 | 4 | 4 | 3 | Replacement of damaged carpark lighting | 5 | 1 | lot | 0.3 | 3171875 |  | 1 | 0 | 0 | 0 | 951562.5 | 0 | 0 |  |  |  | market rate
SMC-042 | Street Lighting | General Lighting and Power System | 1.) 30% of street lighting cover were damaged. 2.) 20% of the street lights were not working. 3.) No spares for Lighting Bulbs & Fixtures. | Typhoon Odette "Rai" | GMCAC | Thirdy Party | Terminal 2 | General | General | General | Electrical | 2018 | 4 | 4 | 4 | 4 | 3 | replacement of damaged street lighting | 5 | 1 | lot | 0.3 | 4531250 |  | 1 | 0 | 0 | 0 | 1359375 | 0 | 0 |  |  |  | assumed 50 street lights
SMC-043 | Directional Signages | General Lighting and Power System | 1.) 10-15% of directional signages were damaged and not working. | Typhoon Odette "Rai" | GMCAC | Thirdy Party | Terminal 2 | General | General | General | Electrical | 2018 | 4 | 4 | 4 | 4 | 3 | replacement of damaged directional signages | 5 | 1 | lot | 0.15 | 270000 |  | 1 | 0 | 0 | 0 | 40500 | 0 | 0
SMC-044 | High Mast Lighting | General Lighting and Power System | 1.) 2 out 11 poles for high mast lightings were already damaged. 2.) 6 out of 11 high mast lightings in terminal 2 had defective lightings. 3.) No spares for Lighting Bulbs & Fixtures. | Typhoon Odette "Rai" | GMCAC | Thirdy Party | Terminal 2 | Apron | All Zone | General | Electrical | 2018 | 4 | 4 | 4 | 4 | 3 | Replacement of damaged high mast lighting | 5 | 1 | lot | 0.2 | 10312500 |  | 1 | 0 | 0 | 0 | 2062500 | 0 | 0 |  |  |  | Cost Database (8 floodlights per pole)
SMC-045 | Uninterruptible Power Supply | Low Voltage Distribution | 1.) 2 out of 4 UPS were damaged by Typhoon Odette. 2.) The UPS can accommodate 100% load of the critical and IT Systems. | Typhoon Odette "Rai" | GMCAC | Thirdy Party | Terminal 2 | Arrival | Zone E4 | UPS Room | Electrical | 2018 | 4 | 4 | 4 | 4 | 3 | corrective maintenance of damaged UPS | 2 | 4 | no | 0.5 | 2087925 |  | 1 | 0 | 0 | 0 | 4175850 | 0 | 0 |  |  |  | Cost Database
SMC-046 | Outlets | General Lighting and Power System | 1.) Generally, the power outlets are in good condition |  | GMCAC | Thirdy Party | Terminal 2 | General | General | General | Electrical | 2018 | 2 | 2 | 2 | 2 | 1 | preventive maintenance | 1 | 1 | lot | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | no cost; part of OPEX
SMC-047 | Normal Lighting | General Lighting and Power System | 1.) 30% of the total architectural lighting were already busted. 2.) Preventive and corrective maintenance of normal lightings is not easily accessible and doable due to high ceilings. 3.) No spares for Lighting Bulbs & Fixtures. | Typhoon Odette "Rai" | GMCAC | Thirdy Party | Terminal 2 | General | General | General | Electrical | 2018 | 4 | 4 | 4 | 4 | 3 | replacement of damaged normal / architectural lightings | 5 | 1 | lot | 0.3 | 20000000 |  | 1 | 0 | 0 | 0 | 6000000 | 0 | 0 |  |  |  | Cost Database
SMC-048 | Junction box and Pull box | General Lighting and Power System | 1.) 20% of the total junction box were uncovered. 2.) 2% of the pullbox enclosure were damaged. | Damage | GMCAC | Thirdy Party | Terminal 2 | General | General | General | Electrical | 2018 | 3 | 3 | 4 | 4 | 2 | replacement of damaged junction box and pull box | 5 | 1 | lot | 0.2 | 600000 |  | 1 | 0 | 0 | 0 | 120000 | 0 | 0 |  |  |  | Cost Database
DDD-001 | Sprinkler heads and pipes | Fire Protection System | Sprinklers and pipes are generally in good condition. |  | GMCAC | Thirdy Party | Terminal 2 | Basement | All Zone | General | Mechanical | 2018 | 2 | 2 | 1 | 2 | 1 | DN | 1 | 1 | lot | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
DDD-004 | Sprinkler heads and pipes | Fire Protection System | Sprinklers and pipes are generally in good condition. |  | GMCAC | Thirdy Party | Terminal 2 | Apron | All Zone | General | Mechanical | 2018 | 2 | 2 | 1 | 2 | 1 | DN | 1 | 1 | lot | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
DDD-028 | Sprinkler heads and pipes | Fire Protection System | Minor leakages and deterioration are found in the reducer. | Damage | GMCAC | Thirdy Party | Terminal 2 | Arrival | Zone D3 | General | Mechanical | 2018 | 4 | 3 | 4 | 4 | 2 | Repair or replace the deteriorated reducer. | 4 | 1 | unit | 1 | 20000 |  | 1 | 0 | 0 | 0 | 20000 | 0 | 0
DDD-023 | Sprinkler heads and pipes | Fire Protection System | Sprinklers and pipes are generally in good condition. |  | GMCAC | Thirdy Party | Terminal 2 | Arrival | All Zone | General | Mechanical | 2018 | 2 | 2 | 1 | 2 | 1 | DN | 1 | 1 | lot | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
DDD-042 | Sprinkler heads and pipes | Fire Protection System | Sprinklers and pipes are generally in good condition. |  | GMCAC | Thirdy Party | Terminal 2 | Departure | All Zone | General | Mechanical | 2018 | 2 | 2 | 1 | 2 | 1 | DN | 1 | 1 | lot | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
DDD-060 | Portable Fire Extinguisher | Fire Protection System | Carbon Dioxide Portable Fire Extinguisher is in good condition. Its scheduled hydrostatic testing or replacement is near. | Aging | GMCAC | Thirdy Party | Terminal 2 | Basement | Zone E2 | Pump Room | Mechanical | 2018 | 4 | 4 | 4 | 4 | 2 | Replace the Carbon dioxide portable fire extinguisher on the 5th year or on 2023. | 5 | 57 | unit | 1 | 7550 |  | 1 | 0 | 0 | 0 | 430350 | 0 | 0
VVL-001 | Fire Hose Cabinet | Fire Protection System | The fire hose cabinets without updated inspection tags are generally in good condition. |  | GMCAC | Thirdy Party | Terminal 2 | Apron | All Zone | General | Mechanical | 2018 | 2 | 2 | 1 | 2 | 1 | DN | 1 | 39 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
DDD-103 | Fire Hose Cabinet | Fire Protection System | The fire hose cabinets without updated inspection tags are generally in good condition. |  | GMCAC | Thirdy Party | Terminal 2 | Arrival | All Zone | General | Mechanical | 2018 | 2 | 2 | 1 | 2 | 1 | DN | 1 | 42 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
DDD-117 | Fire Hose Cabinet | Fire Protection System | The fire hose cabinets without updated inspection tags are generally in good condition. |  | GMCAC | Thirdy Party | Terminal 2 | Departure | All Zone | General | Mechanical | 2018 | 2 | 2 | 1 | 2 | 1 | DN | 1 | 37 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
VVL-021 | Fire Hydrant | Fire Protection System | The fire hydrant is generally in good condition. |  | GMCAC | Thirdy Party | Terminal 2 | Apron | All Zone | General | Mechanical | 2018 | 2 | 2 | 1 | 2 | 1 | DN | 1 | 15 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
DDD-134 | Jockey Pump | Fire Protection System | The jockey pump is generally in good condition. |  | GMCAC | Thirdy Party | Terminal 2 | Basement | Zone E3 | Pump Room | Mechanical | 2018 | 2 | 2 | 1 | 2 | 1 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
DDD-135 | Fire Pumps | Fire Protection System | The fire pumps are generally in good condition. |  | GMCAC | Thirdy Party | Terminal 2 | Basement | Zone E3 | Pump Room | Mechanical | 2018 | 2 | 2 | 1 | 2 | 1 | DN | 1 | 2 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
DDD-136 | Fire Tank | Fire Protection System | The fire tank is generally in good condition. |  | GMCAC | Thirdy Party | Terminal 2 | Basement | Zone E3 | Pump Room | Mechanical | 2018 | 2 | 2 | 1 | 2 | 1 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
DDD-137 | Chiller 1 & 2 | MVAC System | Still provide adequate LOS and in good condition |  | GMCAC | Thirdy Party | Terminal 1 | Arrival | Zone A2 | Chiller Plant Room | Mechanical | 2013 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1 | lot | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
DDD-139 | Chiller 3 | MVAC System | VFD controller and contactor are defective. | Damage | GMCAC | Thirdy Party | Terminal 1 | Arrival | Zone A2 | Chiller Plant Room | Mechanical | 2013 | 4 | 4 | 3 | 4 | 3 | Repair the VFD controller. | 4 | 1 | unit | 1 | 380000 |  | 1 | 0 | 0 | 0 | 380000 | 0 | 0
DDD-140 | Chiller 4 | MVAC System | Condenser tube is leaking. | Damage | GMCAC | Thirdy Party | Terminal 1 | Arrival | Zone A2 | Chiller Plant Room | Mechanical | 2013 | 4 | 4 | 3 | 4 | 3 | Repair the condenser tube | 5 | 1 | unit | 1 | 1170000 |  | 1 | 0 | 0 | 0 | 1170000 | 0 | 0
DDD-141 | Cooling Tower 1 to 4 | MVAC System | This can operate but with minor issues such as damaged protective screens and corrosions. | Damage | GMCAC | Thirdy Party | Terminal 1 | Departure | Zone A2 | Cooling Tower Space | Mechanical | 2012 | 3 | 2 | 3 | 3 | 2 | Repair the protective screens and corrosions. | 3 | 4 | unit | 1 | 87000 |  | 1 | 0 | 0 | 0 | 348000 | 0 | 0
DDD-145 | AHU-NPP1-1, -1, -2, -3 | MVAC System | Insulations are damaged due to typhoon Rai (Odette) but the unit can still operate. | Typhoon Odette "Rai" | GMCAC | Thirdy Party | Terminal 1 | Roof Level | All Zone | Roofdeck | Mechanical | 2019 | 3 | 2 | 3 | 2 | 3 | Repair the insulations | 3 | 1 | lot | 1 | 140000 |  | 1 | 0 | 0 | 0 | 140000 | 0 | 0 | Damaged by Typhoon Rai
DDD-149 | Safety Issue with the Chiller | MVAC System | The chiller room is also used as storage. 5s is not practiced properly. |  | GMCAC | Internal Team | Terminal 1 | Arrival | Zone A2 | Chiller Plant Room | Mechanical | 2013 | 1 | 1 | 1 | 1 | 3 | Clean and practice 5S in the room. | 2 | 1 | lot | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Fire Hazard/Maintenance Issue
DDD-150 | Insulation of chilled water pipes | MVAC System | Deteriorating insulation and molds were observed. | Damage | GMCAC | Internal Team | Terminal 1 | Arrival | Zone A2 | Chiller Plant Room | Mechanical | 2013 | 3 | 3 | 3 | 3 | 2 | Repair the insulations | 3 | 1 | lot | 1 | 177900 |  | 1 | 0 | 0 | 0 | 177900 | 0 | 0
DDD-151 | Insulation of air ducts | MVAC System | Deteriorating insulation and molds were observed. | Damage | GMCAC | Internal Team | Terminal 1 | Arrival | Zone A2 | Chiller Plant Room | Mechanical | 2013 | 3 | 3 | 3 | 3 | 2 | Repair the insulations | 3 | 1 | lot | 1 | 147000 |  | 1 | 0 | 0 | 0 | 147000 | 0 | 0
DDD-152 | 2 valves | MVAC System | Marks of leakages were found in two valves. | Damage | GMCAC | Thirdy Party | Terminal 1 | Arrival | Zone A2 | Chiller Plant Room | Mechanical | 2013 | 3 | 3 | 3 | 3 | 2 | Repair the valves | 3 | 2 | unit | 1 | 449400 |  | 1 | 0 | 0 | 0 | 898800 | 0 | 0
DDD-153 | AHUs | MVAC System | Aging | Aging | GMCAC | Thirdy Party | Terminal 1 | Arrival | General | General | Mechanical | 1994 | 4 | 4 | 4 | 4 | 3 | Major preventive intervention | 4 | 7 | unit | 1 | 500000 |  | 1 | 0 | 1 | 0 | 0 | 3500000 | 0
DDD-158 | Insulation of air ducts | MVAC System | Aging | Aging | GMCAC | Thirdy Party | Terminal 1 | Departure | General | General | Mechanical | 1994 | 4 | 4 | 4 | 4 | 3 | Major preventive intervention | 3 | 1 | lot | 1 | 147000 |  | 1 | 0 | 1 | 0 | 0 | 147000 | 0
DDD-159 | Insulation of chilled water pipes | MVAC System | Aging | Aging | GMCAC | Thirdy Party | Terminal 1 | Departure | General | General | Mechanical | 1994 | 4 | 4 | 4 | 4 | 3 | Major preventive intervention | 3 | 1 | lot | 1 | 177900 |  | 1 | 0 | 1 | 0 | 0 | 177900 | 0
DDD-162 | Portable Fire Extinguisher | Fire Protection System | It is estimated that the portable fire extinguishers were not inspected monthly as specified in NFPA 10. | Damage | GMCAC | Thirdy Party | Terminal 1 | Departure | General | General | Mechanical | 2019 | 3 | 3 | 3 | 3 | 3 | External and internal inspections of the fire extinguishers are required. Replacement of defective fire extinguishers is most likely. | 3 | 1 | lot | 1 | 25000 |  | 1 | 0 | 0 | 0 | 25000 | 0 | 0
DDD-163 | Fire Protection Pipe Supports | Fire Protection System | Buckling and irregular edges are present in the supports of pipes. | Damage | GMCAC | Thirdy Party | Terminal 1 | Arrival | Zone E1 | General | Mechanical | 2019 | 3 | 3 | 3 | 3 | 3 | Repair the existing supports and provide additional supports as necessary. | 3 | 1 | lot | 1 | 500000 |  | 1 | 0 | 0 | 0 | 500000 | 0 | 0 | Assumed all supports to be repaired or replaced.
RAS-001 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | GMCAC | Third Party | Terminal 2 | Apron | Zone C2 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1384.87 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-002 | Drinking Fountain | Plumbing System | Drinking Fountains are working properly. |  | GMCAC | Third Party | Terminal 2 | Apron | Zone C2 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1384.87 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-003 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | GMCAC | Third Party | Terminal 2 | Apron | Zone D1 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1420.77 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-004 | Drinking Fountain | Plumbing System | Drinking Fountains are working properly. |  | GMCAC | Third Party | Terminal 2 | Apron | Zone D1 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1420.77 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-005 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | GMCAC | Third Party | Terminal 2 | Apron | Zone E2 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 647.47 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-006 | Drinking Fountain | Plumbing System | Drinking Fountains are working properly. |  | GMCAC | Third Party | Terminal 2 | Apron | Zone E2 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 647.47 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-007 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | GMCAC | Third Party | Terminal 2 | Apron | Zone E4 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 697.8 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-008 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | GMCAC | Third Party | Terminal 2 | Apron | Zone F1 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1502.34 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-009 | Drinking Fountain | Plumbing System | Drinking Fountains are working properly. |  | GMCAC | Third Party | Terminal 2 | Apron | Zone F1 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1502.34 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-010 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | GMCAC | Third Party | Terminal 2 | Apron | Zone F2 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1464.13 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-011 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | GMCAC | Third Party | Terminal 2 | Apron | Zone F4 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 490.23 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-012 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | GMCAC | Third Party | Terminal 2 | Apron | Zone G1 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1591.09 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-013 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | GMCAC | Third Party | Terminal 2 | Apron | Zone G3 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 536.8 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-014 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | GMCAC | Third Party | Terminal 2 | Apron | Zone K1 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 617.15 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-015 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | GMCAC | Third Party | Terminal 2 | Apron | Zone K1 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 617.15 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-016 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | GMCAC | Third Party | Terminal 2 | Arrival | Zone C2 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1396.36 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-017 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | GMCAC | Third Party | Terminal 2 | Arrival | Zone C4 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1394.98 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-018 | Drinking Fountain | Plumbing System | Drinking Fountains are working properly. |  | GMCAC | Third Party | Terminal 2 | Arrival | Zone C4 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 2 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-019 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | GMCAC | Third Party | Terminal 2 | Arrival | Zone D1 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1402.74 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-020 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | GMCAC | Third Party | Terminal 2 | Arrival | Zone E1 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 236.68 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-021 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | GMCAC | Third Party | Terminal 2 | Arrival | Zone F1 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1445.4 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-022 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | GMCAC | Third Party | Terminal 2 | Arrival | Zone F2 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1463.59 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-023 | Drinking Fountain | Plumbing System | Drinking Fountains are working properly. |  | GMCAC | Third Party | Terminal 2 | Arrival | Zone F2 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 2 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-024 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | GMCAC | Third Party | Terminal 2 | Arrival | Zone F4 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1383.7 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-025 | Drinking Fountain | Plumbing System | Drinking Fountains are working properly. |  | GMCAC | Third Party | Terminal 2 | Arrival | Zone F4 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 4 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-026 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | GMCAC | Third Party | Terminal 2 | Arrival | Zone G1 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1668.32 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-027 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | GMCAC | Third Party | Terminal 2 | Arrival | Zone G2 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1480.83 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-028 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | GMCAC | Third Party | Terminal 2 | Arrival | Zone G3 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1612.18 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-029 | Drinking Fountain | Plumbing System | Drinking Fountains are working properly. |  | GMCAC | Third Party | Terminal 2 | Arrival | Zone G3 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 4 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-030 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | GMCAC | Third Party | Terminal 2 | Arrival | Zone K1 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1153.09 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-031 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | GMCAC | Third Party | Terminal 2 | Arrival | Zone C4 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1394.98 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-032 | Drinking Fountain | Plumbing System | Drinking Fountains are working properly. |  | GMCAC | Third Party | Terminal 2 | Arrival | Zone C4 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 4 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-033 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | GMCAC | Third Party | Terminal 2 | Arrival | Zone D3 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1385.13 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-034 | Drinking Fountain | Plumbing System | Drinking Fountains are working properly. |  | GMCAC | Third Party | Terminal 2 | Arrival | Zone D3 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 4 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-035 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | GMCAC | Third Party | Terminal 2 | Arrival | Zone F1 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1445.4 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-036 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | GMCAC | Third Party | Terminal 2 | Arrival | Zone F2 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1463.59 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-037 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | GMCAC | Third Party | Terminal 2 | Arrival | Zone G1 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1668.32 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-038 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | GMCAC | Third Party | Terminal 2 | Arrival | Zone G2 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1480.83 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-039 | Drinking Fountain | Plumbing System | Drinking Fountains are working properly. |  | GMCAC | Third Party | Terminal 2 | Arrival | Zone G2 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 4 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-040 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | GMCAC | Third Party | Terminal 2 | Arrival | Zone H1 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1063.65 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-041 | Drinking Fountain | Plumbing System | Drinking Fountains are working properly. |  | GMCAC | Third Party | Terminal 2 | Arrival | Zone H1 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 4 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-042 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | GMCAC | Third Party | Terminal 2 | Arrival | Zone H1 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1063.65 | m2 | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-043 | Drinking Fountain | Plumbing System | Drinking Fountains are working properly. |  | GMCAC | Third Party | Terminal 2 | Arrival | Zone H1 | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 2 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-044 | Aircon Water Supply System | Plumbing System | Pumps are working properly. No notable leaks and vibration. |  | GMCAC | Third Party | Terminal 2 | Basement | Zone E1 | Utility Room | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-045 | Domestic Water Supply System | Plumbing System | Pumps are working properly. No notable leaks and vibration. |  | GMCAC | Third Party | Terminal 2 | Basement | Zone E1 | Utility Room | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-046 | Drinking Water Supply System | Plumbing System | Pumps are working properly. No notable leaks and vibration. |  | GMCAC | Third Party | Terminal 2 | Basement | Zone E1 | Utility Room | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 2 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-047 | Domestic Water Supply System for T1 | Plumbing System | Pumps are working properly. No notable leaks and vibration. |  | GMCAC | Third Party | Terminal 2 | Basement | Zone E1 | Utility Room | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | As-built drawing to be updated to include the additional booster system for Terminal 1 | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-048 | Foul Water Treatment Plant | STP System | Effleunt quality more than the allowable threshold. Poorly maintained system. Broken flowmeter. | Damage | MCIAA | Third Party | General | General | All Zone | Foul Water Treatment Plant | Environment | 1990 | 4 | 3 | 3 | 4 | 3 | Upgrade the STP to BNR treatment process and should complied with latest DAO regulation. | 4 | 1 | lot | 1 | 24543300 |  | 1 | 0 | 0 | 0 | 24543300 | 0 | 0
RAS-049 | MVAC Ducting and Appurtenances | MVAC System | Ducting and appurtenances have good insulation and no leaks were detected |  | GMCAC | Third Party | Terminal 2 | Apron | All Zone | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1 | lot | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-125 | Chiller System | MVAC System | Chiller system in good condition, no visible leaks detected |  | GMCAC | Third Party | Terminal 2 | Others | Other | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 4 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-126 | Cooling Tower System | MVAC System | Noticeable corrosion on the body of the cooling towers | Damage | GMCAC | Third Party | Terminal 2 | Others | Other | Utility Building | Mechanical | 2018 | 3 | 3 | 2 | 2 | 1 | Repainting | 2 | 4 | unit | 1 | 25000 |  | 1 | 0 | 0 | 0 | 100000 | 0 | 0
RAS-127 | Chiller 'Pump System | MVAC System | Pump System still in good condition except for a 1 rotary pump |  | GMCAC | Third Party | Terminal 2 | Others | Other | Utility Building | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 10 | unit | 0.2 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-128 | Computer Room Air-Conditioning System | MVAC System | Asset in good condition |  | GMCAC | Third Party | Terminal 2 | Others | Other | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 9 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-129 | Primary Air Handling Unit | MVAC System | Asset in good condition |  | GMCAC | Third Party | Terminal 2 | Others | Other | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 4 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-130 | Air Handling Unit | MVAC System | Asset in good condition, drain lines needs to be properly colored or protection to avoid trip hazard. |  | GMCAC | Third Party | Terminal 2 | Others | Other | General | Mechanical | 2018 | 2 | 2 | 2 | 2 | 1 | DN | 2 | 40 | unit | 0.05 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAS-131 | Plumbing Pipeline and Appurtenances | Plumbing System | No leaks were detected and pressure is within standards. |  | GMCAC | Third Party | Terminal 1 | Arrival | All Zone | General | Mechanical | 1990 | 2 | 2 | 2 | 2 | 1 | DN | 1 | 1 | lot | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-001 | PBB 1 | Passenger Boarding Bridge (PBB) | Damaged Slat Curtain and Aluminum Ceiling on Cabin and Rotunda is an eye-sore. Rainwater may sip through the ceiling if not correctly replaced. | Typhoon Odette "Rai" | GMCAC | Third Party | Terminal 1 | Departure | All Zone | Gangway | Mechanical | 2013 | 3 | 2 | 3 | 2 | 2 | Repair damaged part ensure presentability of bridge to passengers. | 3 | 1 | set | 0.1 | 15000000 |  | 1 | 0 | 0 | 0 | 1500000 | 0 | 0
JMR-002 | PBB 2 | Passenger Boarding Bridge (PBB) | Damaged Slat Curtain and Aluminum Ceiling on Cabin is an eye-sore. Rainwater may sip through the ceiling if not correctly replaced. | Typhoon Odette "Rai" | GMCAC | Third Party | Terminal 1 | Departure | All Zone | Gangway | Mechanical | 2013 | 3 | 2 | 3 | 2 | 2 | Repair damaged part ensure presentability of bridge to passengers. | 3 | 1 | set | 0.1 | 15000000 |  | 1 | 0 | 0 | 0 | 1500000 | 0 | 0
JMR-003 | PBB 3 | Passenger Boarding Bridge (PBB) | Damaged Slat Curtain and Aluminum Ceiling on Cabin is an eye-sore. Rainwater may sip through the ceiling if not correctly replaced. | Typhoon Odette "Rai" | GMCAC | Third Party | Terminal 1 | Departure | All Zone | Gangway | Mechanical | 2013 | 3 | 2 | 3 | 2 | 2 | Repair damaged part ensure presentability of bridge to passengers. | 3 | 1 | set | 0.1 | 15000000 |  | 1 | 0 | 0 | 0 | 1500000 | 0 | 0
JMR-004 | PBB 4 | Passenger Boarding Bridge (PBB) | Damaged Slat Curtain and Aluminum Ceiling on Cabin is an eye-sore. Rainwater may sip through the ceiling if not correctly replaced. | Typhoon Odette "Rai" | GMCAC | Third Party | Terminal 1 | Departure | All Zone | Gangway | Mechanical | 2013 | 3 | 2 | 3 | 2 | 2 | Repair damaged part ensure presentability of bridge to passengers. | 3 | 1 | set | 0.1 | 15000000 |  | 1 | 0 | 0 | 0 | 1500000 | 0 | 0
JMR-005 | PBB 5 | Passenger Boarding Bridge (PBB) | Damaged Slat Curtain and Aluminum Ceiling on Cabin and Rotunda is an eye-sore. Rainwater may sip through the ceiling if not correctly replaced. | Typhoon Odette "Rai" | GMCAC | Third Party | Terminal 1 | Departure | All Zone | Gangway | Mechanical | 2013 | 3 | 2 | 3 | 2 | 2 | Repair damaged part ensure presentability of bridge to passengers. | 3 | 1 | set | 0.1 | 15000000 |  | 1 | 0 | 0 | 0 | 1500000 | 0 | 0
JMR-006 | PBB 6 | Passenger Boarding Bridge (PBB) | Condemned. Parts were cannibalized for other bridges. | Typhoon Odette "Rai" | GMCAC | Third Party | Terminal 1 | Departure | All Zone | Gangway | Mechanical | 2013 | 5 | 3 | 5 | 5 | 5 | Procure parts and restore bridge to ensure equipment is ready for use. | 5 | 1 | set | 0.3 | 50000000 |  | 1 | 0 | 0 | 0 | 15000000 | 0 | 0
JMR-007 | Weighing Conveyors - (53 units) | Baggage Handling System (BHS) | Weighing Conveyors are calibrated on an Annual basis. Calibration should increase to semi-annual period to assure load cell is properly calibrated. |  | GMCAC | Third Party | Terminal 1 | Departure | All Zone | Check-In Hall | Mechanical | 2015 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 53 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
DDD-001 | Software for the BHS system | Baggage Handling System (BHS) | Software is outdated and may affect correct operation of equipment and the whole system. | Aging | GMCAC | Third Party | Terminal 1 | Others | All Zone | General | IT | 2015 | 4 | 4 | 4 | 4 | 3 | Renewal of software system for the BHS | 5 | 1 | lot | 1 | 500000 |  | 1 | 0 | 0 | 0 | 500000 | 0 | 0
JMR-008 | Delivery Conveyors - (8 units) | Baggage Handling System (BHS) | Equipment not maintained by OEM, software defect may affect correct operation of equipment and the whole system. |  | GMCAC | Third Party | Terminal 1 | Departure, Buildup | All Zone | Check-In Hall | Mechanical | 2015 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | set | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | assuming specialized softwares
JMR-009 | Power Curves - (22 units) | Baggage Handling System (BHS) | Equipment not maintained by OEM, software defect may affect correct operation of equipment and the whole system. |  | GMCAC | Third Party | Terminal 1 | Departure, Buildup | All Zone | Build-Up Area | Mechanical | 2015 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 22 | set | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-010 | Plough Diverters (Horizontal) - (6 units) | Baggage Handling System (BHS) | Equipment not maintained by OEM, software defect may affect correct operation of equipment and the whole system. |  | GMCAC | Third Party | Terminal 1 | Departure, Buildup | All Zone | Build-Up Area | Mechanical | 2015 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 4 | set | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-011 | Race Track (Make-up Carousel) - (4 units) | Baggage Handling System (BHS) | Equipment not maintained by OEM, software defect may affect correct operation of equipment and the whole system. |  | GMCAC | Third Party | Terminal 1 | Departure, Buildup | All Zone | Build-Up Area | Mechanical | 2015 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 2 | set | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-012 | Manual Encode Conveyors - (2 units) | Baggage Handling System (BHS) | Equipment not maintained by OEM, software defect may affect correct operation of equipment and the whole system. |  | GMCAC | Third Party | Terminal 1 | Departure, Buildup | All Zone | Build-Up Area | Mechanical | 2015 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 2 | set | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-013 | ETD Line - (2 units) | Baggage Handling System (BHS) | Equipment not maintained by OEM, software defect may affect correct operation of equipment and the whole system. |  | GMCAC | Third Party | Terminal 1 | Departure, Buildup | All Zone | Build-Up Area | Mechanical | 2015 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 4 | set | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-014 | CB (Clear Bag) Line - (4 units) | Baggage Handling System (BHS) | Equipment not maintained by OEM, software defect may affect correct operation of equipment and the whole system. |  | GMCAC | Third Party | Terminal 1 | Departure, Buildup | All Zone | Build-Up Area | Mechanical | 2015 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | set | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-015 | Merge Conveyors - (1 units) | Baggage Handling System (BHS) | Equipment not maintained by OEM, software defect may affect correct operation of equipment and the whole system. |  | GMCAC | Third Party | Terminal 1 | Departure, Buildup | All Zone | Build-Up Area | Mechanical | 2015 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 2 | set | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-016 | Reject Bag Line - (2 units) | Baggage Handling System (BHS) | Equipment not maintained by OEM, software defect may affect correct operation of equipment and the whole system. |  | GMCAC | Third Party | Terminal 1 | Departure, Buildup | All Zone | Build-Up Area | Mechanical | 2015 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 2 | set | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-017 | Automatic Tag Reader - (2 units) | Baggage Handling System (BHS) | Equipment not maintained by OEM, software defect may affect correct operation of equipment and the whole system. |  | GMCAC | Third Party | Terminal 1 | Departure, Buildup | All Zone | Build-Up Area | Mechanical | 2015 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 6 | set | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-018 | Race Track (Arrival Carousel) - (6 units) | Baggage Handling System (BHS) | Equipment not maintained by OEM, software defect may affect correct operation of equipment and the whole system. |  | GMCAC | Third Party | Terminal 1 | Arrival, Apron | All Zone | Baggage Re-Claim | Mechanical | 2015 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | set | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-019 | Initial Check - Stand Alone Dual View X-Ray (Smith) - (2 units) | Security and Screening Devices (SSD) | Equipment highly dependent on proprietary software and hardware of OEM. May cause problem if contract and support from OEM is ceased. |  | GMCAC | Third Party | Terminal 1 | Departure | All Zone | Check-In Hall | Electronics | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 2 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-020 | Initial Check - Stand Alone Dual View X-Ray (Smith) - (2 units) | Security and Screening Devices (SSD) | Equipment highly dependent on proprietary software and hardware of OEM. May cause problem if contract and support from OEM is ceased. |  | GMCAC | Third Party | Terminal 1 | Departure | All Zone | Check-In Hall | Electronics | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 2 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-021 | Final Check - Automatic Tray Return System (Rapiscan) - (4 units) | Security and Screening Devices (SSD) | Equipment highly dependent on proprietary software and hardware of OEM. May cause problem if contract and support from OEM is ceased. |  | GMCAC | Third Party | Terminal 1 | Departure | All Zone | Gangway | Electronics | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 4 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-022 | In-Line Hold Baggage Screening (Rapiscan) - (2 units) | Security and Screening Devices (SSD) | Equipment highly dependent on proprietary software and hardware of OEM. May cause problem if contract and support from OEM is ceased. |  | GMCAC | Third Party | Terminal 1 | Departure, Buildup | All Zone | Final Check | Electronics | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 2 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-023 | In-Line Hold Baggage Screening Confirmatory (Rapiscan) - (1 units) | Security and Screening Devices (SSD) | Equipment highly dependent on proprietary software and hardware of OEM. May cause problem if contract and support from OEM is ceased. |  | GMCAC | Third Party | Terminal 1 | Departure, Buildup | All Zone | Build-Up Area | Electronics | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-024 | Delivery - Stand Alone Dual View (Rapiscan) - (1 units) | Security and Screening Devices (SSD) | Equipment highly dependent on proprietary software and hardware of OEM. May cause problem if contract and support from OEM is ceased. |  | GMCAC | Third Party | Terminal 1 | Departure, Buildup | All Zone | Build-Up Area | Electronics | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-025 | Stand-Alone Hold Baggage Screening (Rapiscan) - (1 units) | Security and Screening Devices (SSD) | Equipment highly dependent on proprietary software and hardware of OEM. May cause problem if contract and support from OEM is ceased. |  | GMCAC | Third Party | Terminal 1 | Departure | All Zone | Build-Up Area | Electronics | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-026 | Employee Entrace - Dual View (Smith) - (1 units) | Security and Screening Devices (SSD) | Equipment highly dependent on proprietary software and hardware of OEM. May cause problem if contract and support from OEM is ceased. |  | GMCAC | Third Party | Terminal 1 | Departure | All Zone | Entrance | Electronics | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-027 | Escalator ES-2 | Vertical Transportation System (VTS) | Ageing of equipment starts to show sign of wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | GMCAC | Third Party | Terminal 1 | Apron, Arrival, Departure | All Zone | Terminal Building | Mechanical | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-028 | Escalator ES-3 | Vertical Transportation System (VTS) | Ageing of equipment starts to show sign of wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | GMCAC | Third Party | Terminal 1 | Apron, Arrival, Departure | All Zone | Terminal Building | Mechanical | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-029 | Escalator ES-4 Hitachi | Vertical Transportation System (VTS) | Ageing of equipment starts to show sign of wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | GMCAC | Third Party | Terminal 1 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-030 | Escalator ES-5 Hitachi | Vertical Transportation System (VTS) | Ageing of equipment starts to show sign of wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | GMCAC | Third Party | Terminal 1 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-031 | Escalator ES-6 | Vertical Transportation System (VTS) | Ageing of equipment starts to show sign of wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | GMCAC | Third Party | Terminal 1 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-032 | Escalator ES-7 | Vertical Transportation System (VTS) | Ageing of equipment starts to show sign of wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | GMCAC | Third Party | Terminal 1 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-033 | Elevator PE-1 | Vertical Transportation System (VTS) | Ageing of equipment starts to show sign of wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | GMCAC | Third Party | Terminal 1 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-034 | Elevator PE-2 | Vertical Transportation System (VTS) | Ageing of equipment starts to show sign of wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | GMCAC | Third Party | Terminal 1 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-035 | Elevator PE-3 | Vertical Transportation System (VTS) | Ageing of equipment starts to show sign of wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | GMCAC | Third Party | Terminal 1 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-036 | Elevator PE-4 | Vertical Transportation System (VTS) | Ageing of equipment starts to show sign of wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | GMCAC | Third Party | Terminal 1 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-037 | Elevator PE-5 | Vertical Transportation System (VTS) | Ageing of equipment starts to show sign of wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | GMCAC | Third Party | Terminal 1 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-038 | Elevator PE-6 | Vertical Transportation System (VTS) | Ageing of equipment starts to show sign of wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | GMCAC | Third Party | Terminal 1 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-039 | Elevator PE-7 | Vertical Transportation System (VTS) | Ageing of equipment starts to show sign of wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | GMCAC | Third Party | Terminal 1 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-040 | Elevator PE-8 | Vertical Transportation System (VTS) | Ageing of equipment starts to show sign of wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | GMCAC | Third Party | Terminal 1 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-041 | SCADA - HVAC | IT System (ITS) | No centralized system that interconnects all SCADA stations. Existing SCADA Station is isolated, no back-up and stored in an unsecured area (small machine room) |  | GMCAC | Third Party | Terminal 1 | Apron | All Zone | SCADA Room | IT | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | lot | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-042 | SCADA - Electrical | IT System (ITS) | No centralized system that interconnects all SCADA stations. Existing SCADA Station is isolated, no back-up and stored in an unsecured area (small machine room) |  | GMCAC | Third Party | Terminal 1 | Apron | All Zone | SCADA Room | IT | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | lot | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-043 | SCADA - Baggage Handling System | IT System (ITS) | No centralized system that interconnects all SCADA stations. Existing SCADA Station is isolated, no back-up and stored in an unsecured area (small machine room). Note that BHS is a critical component of the airport and its IT Systems must be very secured. | Aging | GMCAC | Third Party | Terminal 1 | Apron, Buildup | All Zone | SCADA Room | IT | 2019 | 3 | 3 | 2 | 2 | 2 | Correct issue with Beumer software that equipment is available for use. This is for the integration of the entire airport system. This is considered as new investment including the software, hardwares (e.g. electrical wiring, IT supports). | 1 | 1 | lot | 1 | 20000000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 20000000
JMR-044 | FIDS | IT System (ITS) | FIDS Monitors installed outdoors are lost/damaged due to typhoon. | Typhoon Odette "Rai" | GMCAC | Third Party | Terminal 1 | Apron, Arrival, Departure | All Zone | Whole Terminal Premise | IT | 2019 | 3 | 2 | 3 | 2 | 2 | Install outdoor FIDS in a reinforced setup that will withstand typhoons, OR practice un-installation of FIDS monitors one (1) day before arrival of typhoon. | 3 | 10 | unit | 1 | 280000 |  | 1 | 0 | 0 | 0 | 2800000 | 0 | 0
JMR-045 | CUTE | IT System (ITS) | UPS failed graceful shut-down of Computer Servers during power outtage and run of Generator Sets. This further damaged costly hardware, softwares, and the data/information that should be securely stored. |  | GMCAC | Third Party | Terminal 1 | Apron, Arrival, Departure | All Zone | Check-In Area | IT | 2019 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | lot | 1 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
JMR-046 | CCTV | IT System (ITS) | CCTV equipment installed outdoors are lost/damaged due to typhoon. | Typhoon Odette "Rai" | GMCAC | Third Party | Terminal 1 | Apron, Arrival, Departure | All Zone | Whole Terminal Premise | IT | 2019 | 3 | 3 | 3 | 2 | 2 | Install outdoor CCTVs in a reinforced setup that will withstand typhoons, OR practice un-installation of CCTV equipment one (1) day before arrival of typhoon. | 6 | 15 | unit | 1 | 20000 |  | 1 | 0 | 0 | 0 | 300000 | 0 | 0
JMR-047 | PBB C-13r | Passenger Boarding Bridge (PBB) | Slat Curtain on Cab Area Damaged. Damaged Anti-Collision Sensors and Anti-Shear Sensor was temporarily repaired. Recommend immediate replacement due ensure safety of bridge and aircraft during operation. | Typhoon Odette "Rai" | GMCAC | Third Party | Terminal 2 | Departure | All Zone | Gangway | Mechanical | 2017 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-048 | PBB C-13l | Passenger Boarding Bridge (PBB) | Damaged Anti-Collision Sensor was temporarily repaired. Recommend immediate replacement due to critical component on safety of bridge. | Typhoon Odette "Rai" | GMCAC | Third Party | Terminal 2 | Departure | All Zone | Gangway | Mechanical | 2017 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-049 | PBB C-12r | Passenger Boarding Bridge (PBB) | Damaged Slat Curtain and Aluminum Ceiling on Cab Area | Typhoon Odette "Rai" | GMCAC | Third Party | Terminal 2 | Departure | All Zone | Gangway | Mechanical | 2017 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-050 | PBB C-12l | Passenger Boarding Bridge (PBB) | Damaged Slat Curtain and Aluminum Ceiling on Cab Area | Typhoon Odette "Rai" | GMCAC | Third Party | Terminal 2 | Departure | All Zone | Gangway | Mechanical | 2017 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-051 | PBB C-21 | Passenger Boarding Bridge (PBB) | Damaged Canopies. Rainwater may sip through the aircraft doors if not correctly replaced. Will cause discomfort to passengers during rainy weather. | Typhoon Odette "Rai" | GMCAC | Third Party | Terminal 2 | Departure | All Zone | Gangway | Mechanical | 2017 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-052 | PBB C-22 | Passenger Boarding Bridge (PBB) | Damaged Canopies. Rainwater may sip through the aircraft doors if not correctly replaced. Will cause discomfort to passengers during rainy weather. | Typhoon Odette "Rai" | GMCAC | Third Party | Terminal 2 | Departure | All Zone | Gangway | Mechanical | 2017 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-053 | PBB C-23 | Passenger Boarding Bridge (PBB) | Damaged Canopies. Rainwater may sip through the aircraft doors if not correctly replaced. Will cause discomfort to passengers during rainy weather. | Typhoon Odette "Rai" | GMCAC | Third Party | Terminal 2 | Departure | All Zone | Gangway | Mechanical | 2017 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-054 | Weighing Conveyors - (48 units) | Baggage Handling System (BHS) | Weighing Conveyors are calibrated on an Annual basis. Calibration should increase to semi-annual period to assure load cell is properly calibrated. |  | GMCAC | Third Party | Terminal 2 | Departure, Buildup | All Zone | Check-In Hall | Mechanical | 2015 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 48 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-055 | Delivery Conveyors - (4 units) | Baggage Handling System (BHS) | One (1) line of conveyors are not operational due to repair works |  | GMCAC | Third Party | Terminal 2 | Departure, Buildup | All Zone | Check-In Hall | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 4 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-056 | Power Curves - (31 units) | Baggage Handling System (BHS) | Equipment not maintained by OEM, software defect may affect correct operation of equipment and the whole system. |  | GMCAC | Third Party | Terminal 2 | Departure, Buildup | All Zone | Build-Up Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 31 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-057 | Plough Diverters (Horizontal) - (6 units) | Baggage Handling System (BHS) | Line-1 plough diverter not working due to issue with Beumer software problem |  | GMCAC | Third Party | Terminal 2 | Departure, Buildup | All Zone | Build-Up Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 6 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-058 | Race Track (Make-up Carousel) - (2 units) | Baggage Handling System (BHS) | One (1) set of make-up carousel is not operational due to issue with MVXR (X-Ray) software |  | GMCAC | Third Party | Terminal 2 | Departure, Buildup | All Zone | Build-Up Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 2 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-059 | Manual Encode Conveyors - (1 units) | Baggage Handling System (BHS) | Manual Encoding Station is manual mode due to issue with Beumer software problem |  | GMCAC | Third Party | Terminal 2 | Departure, Buildup | All Zone | Build-Up Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-060 | ETD Line - (2 units) | Baggage Handling System (BHS) | Equipment not maintained by OEM, software defect may affect correct operation of equipment and the whole system. |  | GMCAC | Third Party | Terminal 2 | Departure, Buildup | All Zone | Build-Up Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 2 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-061 | CB (Clear Bag) Line - (2 units) | Baggage Handling System (BHS) | Equipment not maintained by OEM, software defect may affect correct operation of equipment and the whole system. |  | GMCAC | Third Party | Terminal 2 | Departure, Buildup | All Zone | Build-Up Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 2 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-062 | Merge Conveyors - (2 units) | Baggage Handling System (BHS) | Equipment not maintained by OEM, software defect may affect correct operation of equipment and the whole system. |  | GMCAC | Third Party | Terminal 2 | Departure, Buildup | All Zone | Build-Up Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 2 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-063 | Vertical Sorter - (2 units) | Baggage Handling System (BHS) | Equipment not maintained by OEM, software defect may affect correct operation of equipment and the whole system. |  | GMCAC | Third Party | Terminal 2 | Departure, Buildup | All Zone | Build-Up Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 2 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-064 | Reject Bag Line - (1 units) | Baggage Handling System (BHS) | Equipment not maintained by OEM, software defect may affect correct operation of equipment and the whole system. |  | GMCAC | Third Party | Terminal 2 | Departure, Buildup | All Zone | Build-Up Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-065 | Automatic Tag Reader - (2 units) | Baggage Handling System (BHS) | Equipment not maintained by OEM, software defect may affect correct operation of equipment and the whole system. |  | GMCAC | Third Party | Terminal 2 | Departure, Buildup | All Zone | Build-Up Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 2 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-066 | Race Track (Arrival Carousel) - (4 units) | Baggage Handling System (BHS) | Equipment not maintained by OEM, software defect may affect correct operation of equipment and the whole system. |  | GMCAC | Third Party | Terminal 2 | Arrival, Apron | All Zone | Baggage Re-Claim | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 4 | set | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-067 | Stand Alone Dual View X-Ray (Rapiscan) - (5 units) | Security and Screening Devices (SSD) | Equipment highly dependent on proprietary software and hardware of OEM. May cause problem if contract and support from OEM is ceased. |  | GMCAC | Third Party | Terminal 2 | Departure | All Zone | Check-In Hall | Electronics | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 5 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-068 | In-Line Hold Baggage Screening (Rapiscan) - (2 units) | Security and Screening Devices (SSD) | Equipment highly dependent on proprietary software and hardware of OEM. May cause problem if contract and support from OEM is ceased. |  | GMCAC | Third Party | Terminal 2 | Departure | All Zone | Check-In Hall | Electronics | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 2 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-069 | In-bound Check - Stand Alone Dual View X-Ray (Smith) - (1 units) | Security and Screening Devices (SSD) | Equipment highly dependent on proprietary software and hardware of OEM. May cause problem if contract and support from OEM is ceased. |  | GMCAC | Third Party | Terminal 2 | Departure, Buildup | All Zone | Gangway | Electronics | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-070 | Over Size Baggage - Stand Alone Hold Baggage Screeening (Rapiscan) - (1 units) | Security and Screening Devices (SSD) | Equipment highly dependent on proprietary software and hardware of OEM. May cause problem if contract and support from OEM is ceased. |  | GMCAC | Third Party | Terminal 2 | Departure, Buildup | All Zone | Final Check | Electronics | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-071 | Employee Entrace - Dual View (Rapiscan) - (1 units) | Security and Screening Devices (SSD) | Equipment highly dependent on proprietary software and hardware of OEM. May cause problem if contract and support from OEM is ceased. |  | GMCAC | Third Party | Terminal 2 | Departure, Buildup | All Zone | Build-Up Area | Electronics | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-072 | In-Line Hold Baggage Screening Confirmatory (Rapiscan) - (1 units) | Security and Screening Devices (SSD) | Equipment highly dependent on proprietary software and hardware of OEM. May cause problem if contract and support from OEM is ceased. |  | GMCAC | Third Party | Terminal 2 | Departure | All Zone | Build-Up Area | Electronics | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-073 | Explosive Trace Detector (ETD) - (Rapiscan) - (6 units) | Security and Screening Devices (SSD) | Equipment highly dependent on proprietary software and hardware of OEM. May cause problem if contract and support from OEM is ceased. |  | GMCAC | Third Party | Terminal 2 | Departure, Buildup | All Zone | Build-Up Area | Electronics | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 6 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-074 | Walk Through Metal Detectors (WTMD) - (*8 units) | Security and Screening Devices (SSD) | Equipment highly dependent on proprietary software and hardware of OEM. May cause problem if contract and support from OEM is ceased. |  | GMCAC | Third Party | Terminal 2 | Departure | All Zone | Entrance | Electronics | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 8 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-075 | Escalator ES-3 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | GMCAC | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-076 | Escalator ES-4 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | GMCAC | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-077 | Escalator ES-6 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | GMCAC | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-078 | Escalator ES-7 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | GMCAC | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-079 | Escalator ES-8 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | GMCAC | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-080 | Escalator ES-9 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | GMCAC | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-081 | Escalator ES-10 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | GMCAC | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-082 | Escalator ES-11 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | GMCAC | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-083 | Escalator ES-12 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | GMCAC | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-084 | Escalator ES-13 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | GMCAC | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-085 | Escalator ES-14 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | GMCAC | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-086 | Elevator PE-1 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | GMCAC | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-087 | Elevator PE-2 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | GMCAC | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-088 | Elevator PE-3 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | GMCAC | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-089 | Elevator PE-4 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | GMCAC | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-090 | Elevator PE-5 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | GMCAC | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-091 | Elevator PE-6 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | GMCAC | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-092 | Elevator PE-7 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | GMCAC | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-093 | Elevator PE-8 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | GMCAC | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-094 | Elevator PE-9 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | GMCAC | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-095 | Elevator PE-10 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | GMCAC | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-096 | Elevator PE-11 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | GMCAC | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-097 | Elevator PE-12 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | GMCAC | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-098 | Elevator SE-1 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | GMCAC | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-099 | Elevator SE-2 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | GMCAC | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-100 | Elevator SE-3 | Vertical Transportation System (VTS) | Continuous use of equipment is succeptible to typical wear and tear. Practice shut-down of equipment before typhoon to avoid accidents. |  | GMCAC | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Passenger Movement Area | Mechanical | 2018 | 2 | 2 | 2 | 1 | 2 | DN | 1 | 1 | unit | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-101 | SCADA - HVAC | IT System (ITS) | Stand-alone setup. Not linked to Central System. May pose |  | GMCAC | Third Party | Terminal 2 | Apron | All Zone | SCADA Room | IT | 2018 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | lot | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-102 | SCADA - Electrical | IT System (ITS) | Stand-alone setup. Not linked to Central System |  | GMCAC | Third Party | Terminal 2 | Apron | All Zone | SCADA Room | IT | 2018 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | lot | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-103 | SCADA - Baggage Handling System | IT System (ITS) | Stand-alone setup. Not linked to Central System. Problem with Beumer Program. |  | GMCAC | Third Party | Terminal 2 | Apron, Buildup | All Zone | SCADA Room | IT | 2018 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | lot | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-104 | FIDS | IT System (ITS) | FIDS Monitors installed outdoors are lost/damaged due to typhoon. |  | GMCAC | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Whole Terminal Premise | IT | 2018 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | lot | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-105 | CUTE | IT System (ITS) | UPS failed graceful shut-down of Computer Servers during power outtage and run of Generator Sets. This further damaged costly hardware, softwares, and the data/information that should be securely stored. |  | GMCAC | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Check-In Area | IT | 2018 | 2 | 2 | 2 | 2 | 2 | DN | 1 | 1 | lot | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JMR-106 | CCTV | IT System (ITS) | CCTV equipment installed outdoors are lost/damaged due to typhoon. | Typhoon Odette "Rai" | GMCAC | Third Party | Terminal 2 | Apron, Arrival, Departure | All Zone | Whole Terminal Premise | IT | 2018 | 3 | 3 | 3 | 2 | 2 | Install outdoor CCTVs in a reinforced setup that will withstand typhoons, OR practice un-installation of CCTV equipment one (1) day before arrival of typhoon. | 3 | 15 | unit | 1 | 20000 |  | 1 | 0 | 0 | 0 | 300000 | 0 | 0
JMR-107 | AOCC | IT System (ITS) | SCADA of BHS, VAC, Utilities are not integrated. |  | GMCAC | Third Party | Terminal 2 | Departure | All Zone | Central Control Room | IT | 2018 | 3 | 3 | 1 | 1 | 2 | Cost already included in JMR-044 | 1 | 1 | lot | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0
JCF-001 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | GMCAC | Internal Team | Terminal 1 | Departure | Zone A1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 445.65 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 802170 | 0 | 0 | This is also recommended by the seller
JCF-002 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | GMCAC | Internal Team | Terminal 1 | Departure | Zone A2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 883.93 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 1591074 | 0 | 0
JCF-003 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | GMCAC | Internal Team | Terminal 1 | Departure | Zone A4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 305.84 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 550512 | 0 | 0
JCF-004 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | GMCAC | Internal Team | Terminal 1 | Departure | Zone B1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1064.43 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 1915974 | 0 | 0
JCF-005 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | GMCAC | Internal Team | Terminal 1 | Departure | Zone B2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 913.85 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 1644930 | 0 | 0
JCF-006 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | GMCAC | Internal Team | Terminal 1 | Departure | Zone B3 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1383.54 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 2490372 | 0 | 0
JCF-007 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | GMCAC | Internal Team | Terminal 1 | Departure | Zone B4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1154.06 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 2077308 | 0 | 0
JCF-008 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | GMCAC | Internal Team | Terminal 1 | Departure | Zone C1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1113.7 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 2004660 | 0 | 0
JCF-009 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | GMCAC | Internal Team | Terminal 1 | Departure | Zone C2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 992.1 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 1785780 | 0 | 0
JCF-010 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | GMCAC | Internal Team | Terminal 1 | Departure | Zone C3 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1382.79 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 2489022 | 0 | 0
JCF-011 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | GMCAC | Internal Team | Terminal 1 | Departure | Zone C4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1155.58 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 2080044 | 0 | 0
JCF-012 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | GMCAC | Internal Team | Terminal 1 | Departure | Zone D1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1215.21 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 2187378 | 0 | 0
JCF-013 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | GMCAC | Internal Team | Terminal 1 | Departure | Zone D2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1016.77 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 1830186 | 0 | 0
JCF-014 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | GMCAC | Internal Team | Terminal 1 | Departure | Zone D3 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1383.41 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 2490138 | 0 | 0
JCF-015 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | GMCAC | Internal Team | Terminal 1 | Departure | Zone D4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 484.55 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 872190 | 0 | 0
JCF-016 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | GMCAC | Internal Team | Terminal 1 | Departure | Zone E1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1431.54 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 2576772 | 0 | 0
JCF-017 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | GMCAC | Internal Team | Terminal 1 | Departure | Zone E2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1697.69 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 3055842 | 0 | 0
JCF-018 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | GMCAC | Internal Team | Terminal 1 | Departure | Zone F1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1700.03 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 3060054 | 0 | 0
JCF-019 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | GMCAC | Internal Team | Terminal 1 | Departure | Zone F2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1428.08 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 2570544 | 0 | 0
JCF-020 | Waterproofing | Roofing System | Waterproofing reached its end of life resulting to water leak on the below level | Aging | GMCAC | Internal Team | Terminal 1 | Departure | Zone E4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Reapplication of waterproofing | 4 | 1575.71 | m2 | 0.3 | 1000 |  | 1 | 0 | 0 | 0 | 472713 | 0 | 0
JCF-021 | Waterproofing | Roofing System | Waterproofing reached its end of life resulting to water leak on the below level | Aging | GMCAC | Internal Team | Terminal 1 | Departure | Zone F3 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Reapplication of waterproofing | 4 | 1575.04 | m2 | 0.3 | 1000 |  | 1 | 0 | 0 | 0 | 472512 | 0 | 0
JCF-022 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone A1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 445.65 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 2228.25 | 0 | 0
JCF-023 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone A2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 883.93 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 4419.65 | 0 | 0
JCF-024 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone A4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 305.84 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 1529.2 | 0 | 0
JCF-025 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone B1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1064.43 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 5322.15 | 0 | 0
JCF-026 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone B2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 913.85 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 4569.25 | 0 | 0
JCF-027 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone B3 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1383.54 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 6917.7 | 0 | 0
JCF-028 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone B4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1154.06 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 5770.3 | 0 | 0
JCF-029 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone C1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1113.7 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 5568.5 | 0 | 0
JCF-030 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone C2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 992.1 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 4960.5 | 0 | 0
JCF-031 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone C3 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1382.79 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 6913.95 | 0 | 0
JCF-032 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone C4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1155.58 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 5777.9 | 0 | 0
JCF-033 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone D1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1215.21 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 6076.05 | 0 | 0
JCF-034 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone D2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1016.77 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 5083.85 | 0 | 0
JCF-035 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone D3 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1383.41 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 6917.05 | 0 | 0
JCF-036 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone D4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 484.55 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 2422.75 | 0 | 0
JCF-037 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone E1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1431.54 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 7157.7 | 0 | 0
JCF-038 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone E2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1697.69 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 8488.45 | 0 | 0
JCF-039 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone F1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1700.03 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 8500.15 | 0 | 0
JCF-040 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone F2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1428.08 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 7140.4 | 0 | 0
JCF-041 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone A1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 445.65 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 178260 | 0 | 0
JCF-042 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone A2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 883.93 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 353572 | 0 | 0
JCF-043 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone A4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 305.84 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 122336 | 0 | 0
JCF-044 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone B1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1064.43 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 425772 | 0 | 0
JCF-045 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone B2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 913.85 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 365540 | 0 | 0
JCF-046 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone B3 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1383.54 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 553416 | 0 | 0
JCF-047 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone B4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1154.06 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 461624 | 0 | 0
JCF-048 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone C1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1113.7 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 445480 | 0 | 0
JCF-049 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone C2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 992.1 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 396840 | 0 | 0
JCF-050 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone C3 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1382.79 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 553116 | 0 | 0
JCF-051 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone C4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1155.58 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 462232 | 0 | 0
JCF-052 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone D1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1215.21 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 486084 | 0 | 0
JCF-053 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone D2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1016.77 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 406708 | 0 | 0
JCF-054 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone D3 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1383.41 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 553364 | 0 | 0
JCF-055 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone D4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 484.55 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 193820 | 0 | 0
JCF-056 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone E1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1431.54 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 572616 | 0 | 0
JCF-057 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone E2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1697.69 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 679076 | 0 | 0
JCF-058 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone F1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1700.03 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 680012 | 0 | 0
JCF-059 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone F2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1428.08 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 571232 | 0 | 0
JCF-060 | Chiller Structural Steel Supports | Equipment and Machinery Supports | 1) Chiller support are corroded 2) Paints faded away, resulting to steel supports exposed to weather | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone A4 | Cooling Tower | Structural | 1990 | 4 | 4 | 3 | 3 | 1 | Conduct structural evaluation to assess the capacity of the support May undergo retrofitting to increase the strength Esnure proper maintenance for the paint coating | 5 | 305.84 | m2 | 1 | 500 |  | 1 | 0 | 1 | 0 | 0 | 152920 | 0
JCF-061 | Floor Drains | Floor System | Clogged Floor Drains | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone A4 | Passageway | Architectural | 1990 | 3 | 3 | 3 | 3 | 1 | Declogged floor drains, and ensure regular maintenace to avoid the accumulation of debris on the drains | 3 | 305.84 | m2 | 0.3 | 80 |  | 1 | 0 | 0 | 0 | 7340.16 | 0 | 0
JCF-062 | Floor Drains | Floor System | Clogged Floor Drains | Damage | GMCAC | Internal Team | Terminal 1 | Departure | Zone E1 | Passageway | Architectural | 1990 | 3 | 3 | 3 | 3 | 1 | Declogged floor drains, and ensure regular maintenace to avoid the accumulation of debris on the drains | 3 | 1431.54 | m2 | 0.05 | 80 |  | 1 | 0 | 0 | 0 | 5726.16 | 0 | 0
JCF-063 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | GMCAC | Internal Team | Terminal 1 | Arrival | Zone A1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 620.26 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 1116468 | 0 | 0 | Arrival
JCF-064 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | GMCAC | Internal Team | Terminal 1 | Arrival | Zone A2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 954.61 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 1718298 | 0 | 0
JCF-065 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | GMCAC | Internal Team | Terminal 1 | Arrival | Zone A4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 274.87 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 494766 | 0 | 0
JCF-066 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | GMCAC | Internal Team | Terminal 1 | Arrival | Zone B1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1146.19 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 2063142 | 0 | 0
JCF-067 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | GMCAC | Internal Team | Terminal 1 | Arrival | Zone B2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 978.22 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 1760796 | 0 | 0
JCF-068 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | GMCAC | Internal Team | Terminal 1 | Arrival | Zone B3 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1389.9 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 2501820 | 0 | 0
JCF-069 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | GMCAC | Internal Team | Terminal 1 | Arrival | Zone B4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1157.59 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 2083662 | 0 | 0
JCF-070 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | GMCAC | Internal Team | Terminal 1 | Arrival | Zone C1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1128.74 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 2031732 | 0 | 0
JCF-071 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | GMCAC | Internal Team | Terminal 1 | Arrival | Zone C2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1000.72 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 1801296 | 0 | 0
JCF-072 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | GMCAC | Internal Team | Terminal 1 | Arrival | Zone C3 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1390.72 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 2503296 | 0 | 0
JCF-073 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | GMCAC | Internal Team | Terminal 1 | Arrival | Zone C4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1157.87 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 2084166 | 0 | 0
JCF-074 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | GMCAC | Internal Team | Terminal 1 | Arrival | Zone D1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1250.95 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 2251710 | 0 | 0
JCF-075 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | GMCAC | Internal Team | Terminal 1 | Arrival | Zone D2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1054.2 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 1897560 | 0 | 0
JCF-076 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | GMCAC | Internal Team | Terminal 1 | Arrival | Zone D3 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1389.08 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 2500344 | 0 | 0
JCF-077 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | GMCAC | Internal Team | Terminal 1 | Arrival | Zone D4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 309.05 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 556290 | 0 | 0
JCF-078 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | GMCAC | Internal Team | Terminal 1 | Arrival | Zone E1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1356.4 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 2441520 | 0 | 0
JCF-079 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | GMCAC | Internal Team | Terminal 1 | Arrival | Zone E2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1705.18 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 3069324 | 0 | 0
JCF-080 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | GMCAC | Internal Team | Terminal 1 | Arrival | Zone F1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1705.04 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 3069072 | 0 | 0
JCF-081 | Ceiling Tiles | Ceiling System | 1) Uneven ceiling surface/sagging of ceiling boards 2) Stains on the ceiling/discoloration Due to aging that reach its end-of-life | Aging | GMCAC | Internal Team | Terminal 1 | Arrival | Zone F2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Replacement of ceiling and proper disposal of the existing | 5 | 1321.57 | m2 | 1 | 1800 |  | 1 | 0 | 0 | 0 | 2378826 | 0 | 0
JCF-082 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 1 | Arrival | Zone A1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 620.26 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 3101.3 | 0 | 0
JCF-083 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 1 | Arrival | Zone A2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 954.61 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 4773.05 | 0 | 0
JCF-084 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 1 | Arrival | Zone A4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 274.87 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 1374.35 | 0 | 0
JCF-085 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 1 | Arrival | Zone B1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1146.19 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 5730.95 | 0 | 0
JCF-086 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 1 | Arrival | Zone B2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 978.22 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 4891.1 | 0 | 0
JCF-087 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 1 | Arrival | Zone B3 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1389.9 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 6949.5 | 0 | 0
JCF-088 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 1 | Arrival | Zone B4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1157.59 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 5787.95 | 0 | 0
JCF-089 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 1 | Arrival | Zone C1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1128.74 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 5643.7 | 0 | 0
JCF-090 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 1 | Arrival | Zone C2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1000.72 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 5003.6 | 0 | 0
JCF-091 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 1 | Arrival | Zone C3 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1390.72 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 6953.6 | 0 | 0
JCF-092 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 1 | Arrival | Zone C4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1157.87 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 5789.35 | 0 | 0
JCF-093 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 1 | Arrival | Zone D1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1250.95 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 6254.75 | 0 | 0
JCF-094 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 1 | Arrival | Zone D2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1054.2 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 5271 | 0 | 0
JCF-095 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 1 | Arrival | Zone D3 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1389.08 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 6945.4 | 0 | 0
JCF-096 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 1 | Arrival | Zone D4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 309.05 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 1545.25 | 0 | 0
JCF-097 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 1 | Arrival | Zone E1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1356.4 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 6782 | 0 | 0
JCF-098 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 1 | Arrival | Zone E2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1705.18 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 8525.9 | 0 | 0
JCF-099 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 1 | Arrival | Zone F1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1705.04 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 8525.2 | 0 | 0
JCF-100 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 1 | Arrival | Zone F2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1321.57 | m2 | 0.05 | 100 |  | 1 | 0 | 0 | 0 | 6607.85 | 0 | 0
JCF-101 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | GMCAC | Internal Team | Terminal 1 | Arrival | Zone A1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 620.26 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 248104 | 0 | 0
JCF-102 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | GMCAC | Internal Team | Terminal 1 | Arrival | Zone A2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 954.61 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 381844 | 0 | 0
JCF-103 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | GMCAC | Internal Team | Terminal 1 | Arrival | Zone A4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 274.87 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 109948 | 0 | 0
JCF-104 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | GMCAC | Internal Team | Terminal 1 | Arrival | Zone B1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1146.19 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 458476 | 0 | 0
JCF-105 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | GMCAC | Internal Team | Terminal 1 | Arrival | Zone B2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 978.22 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 391288 | 0 | 0
JCF-106 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | GMCAC | Internal Team | Terminal 1 | Arrival | Zone B3 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1389.9 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 555960 | 0 | 0
JCF-107 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | GMCAC | Internal Team | Terminal 1 | Arrival | Zone B4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1157.59 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 463036 | 0 | 0
JCF-108 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | GMCAC | Internal Team | Terminal 1 | Arrival | Zone C1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1128.74 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 451496 | 0 | 0
JCF-109 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | GMCAC | Internal Team | Terminal 1 | Arrival | Zone C2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1000.72 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 400288 | 0 | 0
JCF-110 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | GMCAC | Internal Team | Terminal 1 | Arrival | Zone C3 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1390.72 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 556288 | 0 | 0
JCF-111 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | GMCAC | Internal Team | Terminal 1 | Arrival | Zone C4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1157.87 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 463148 | 0 | 0
JCF-112 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | GMCAC | Internal Team | Terminal 1 | Arrival | Zone D1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1250.95 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 500380 | 0 | 0
JCF-113 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | GMCAC | Internal Team | Terminal 1 | Arrival | Zone D2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1054.2 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 421680 | 0 | 0
JCF-114 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | GMCAC | Internal Team | Terminal 1 | Arrival | Zone D3 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1389.08 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 555632 | 0 | 0
JCF-115 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | GMCAC | Internal Team | Terminal 1 | Arrival | Zone D4 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 309.05 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 123620 | 0 | 0
JCF-116 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | GMCAC | Internal Team | Terminal 1 | Arrival | Zone E1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1356.4 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 542560 | 0 | 0
JCF-117 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | GMCAC | Internal Team | Terminal 1 | Arrival | Zone E2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1705.18 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 682072 | 0 | 0
JCF-118 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | GMCAC | Internal Team | Terminal 1 | Arrival | Zone F1 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1705.04 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 682016 | 0 | 0
JCF-119 | Floor Tiles | Floor System | Damaged and stained floor tiles possibly due to poor maintenace that results to moisture damage | Damage | GMCAC | Internal Team | Terminal 1 | Arrival | Zone F2 | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 1 | Replacement of damage and stained tiles. Ensure proper maintenance to avoid moisture damageed | 5 | 1321.57 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 528628 | 0 | 0
JCF-120 | Facade Glazing | Curtain Wall System | Glazings and its supports was destroyed by Odette or Typhoon "Rai" | Typhoon Odette "Rai" | GMCAC | Internal Team | Terminal 1 | Roof Level | Zone E4 | General | Architectural | 1990 | 5 | 5 | 3 | 3 | 2 | Replaced damaged facaded glazing | 6 | 1575.71 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 630284 | 0 | 0
JCF-121 | Facade Glazing | Curtain Wall System | Glazings and its supports was destroyed by Odette or Typhoon "Rai" | Typhoon Odette "Rai" | GMCAC | Internal Team | Terminal 1 | Roof Level | Zone F3 | General | Architectural | 1990 | 5 | 5 | 3 | 3 | 2 | Replaced damaged facaded glazing | 6 | 1575.04 | m2 | 0.2 | 2000 |  | 1 | 0 | 0 | 0 | 630016 | 0 | 0
JCF-122 | Roof Fabric Sheet, Roof Trusses, Main-Lateral-Frame-System | Structural Framing System | Structural code used for the design was oudated - may not comply to current standards for wind and seismic loadings | Aging | GMCAC | Internal Team | Terminal 1 | Roof Level | All Zone | General | Architectural | 1990 | 4 | 4 | 3 | 3 | 2 | Conduct structural evaluation to comply with the current structural code of the philippines May undergo retrofitting to increase the strength and meet the requirements for current structural code of the philippines | 7 | 1 | lot | 1 | 25000000 |  | 1 | 0 | 0 | 0 | 25000000 | 0 | 0
JCF-1221 | Retrofitting of the structure | Roof Structural Framing System | Damage with cracking and old design | Damage | MCIAA | Internal Team | Terminal 1 | General | All Zone | General | Structural | 1994 | 3 | 3 | 3 | 3 | 3 | Structureal Reforitting | 4 | 1 | lot | 1 | 105000000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 105000000
JCF-181 | Floor Tiles | Floor System | 1) Floor granite tiles are starting to show discoloration deterioration due to ponding of water which is cause of open area with lack of floor drain, drainage and improper sloping for floor 2) Maintenance is expensive due to frequent removal of accumulated water after the rain | Aging | GMCAC | Internal Team | Terminal 2 | Apron | All Zone | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Conduct storm drain study to assess the need to provide additional drainage system on the area. Treat discolored tiles if still possible. Otherwise, replaced damaged tiles. | 7 | 1 | lot | 1 | 2000000 |  | 1 | 0 | 0 | 0 | 2000000 | 0 | 0
JCF-183 | Column | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone A2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 550.29 | m2 | 0.05 | 2000 |  | 1 | 0 | 0 | 0 | 55029 | 0 | 0
JCF-184 | Column | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone B1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 589.71 | m2 | 0.05 | 2000 |  | 1 | 0 | 0 | 0 | 58971 | 0 | 0
JCF-185 | Column | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone A4 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 1439.77 | m2 | 0.05 | 2000 |  | 1 | 0 | 0 | 0 | 143977 | 0 | 0
JCF-186 | Column | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone B3 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 1509.96 | m2 | 0.05 | 2000 |  | 1 | 0 | 0 | 0 | 150996 | 0 | 0
JCF-187 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone A2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 550.29 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 110058 | 0 | 0
JCF-188 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone B1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 589.71 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 117942 | 0 | 0
JCF-189 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone A4 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 1439.77 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 287954 | 0 | 0
JCF-190 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone E2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 647.47 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 129494 | 0 | 0
JCF-191 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone E4 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 697.8 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 139560 | 0 | 0
JCF-192 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone F1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 1502.34 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 300468 | 0 | 0
JCF-193 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone F2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 1464.13 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 292826 | 0 | 0
JCF-194 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone G1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 1591.09 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 318218 | 0 | 0
JCF-195 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone G2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 1594.09 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 318818 | 0 | 0
JCF-196 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone H1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 1128.22 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 225644 | 0 | 0
JCF-197 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone H2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 1130.82 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 226164 | 0 | 0
JCF-198 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone I1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 756.73 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 151346 | 0 | 0
JCF-199 | Beam | Structural Framing System | Damaged and exposed rebar of beam due to removal of canopy | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone B1 | General | Structural | 2018 | 5 | 5 | 4 | 4 | 2 | Conduct structural investigation to assess the strength of the structural membder Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 589.71 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 117942 | 0 | 0
JCF-200 | Louver Support | Architectural Elements Supports | Louver support starting to shows corrosion | Aging | GMCAC | Internal Team | Terminal 2 | Apron | Zone B1 | General | Structural | 2018 | 3 | 3 | 1 | 1 | 1 | Repplication of paint to protect the structural steel support from weather | 3 | 589.71 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 5897.1 | 0 | 0
JCF-201 | Louver Support | Architectural Elements Supports | Louver support starting to shows corrosion | Aging | GMCAC | Internal Team | Terminal 2 | Apron | Zone A2 | General | Structural | 2018 | 3 | 3 | 1 | 1 | 1 | Repplication of paint to protect the structural steel support from weather | 3 | 550.29 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 5502.9 | 0 | 0
JCF-202 | Canopy | Roofing System | Dismantled roofing sheet due to Odette or Typhoon "Rai" | Typhoon Odette "Rai" | GMCAC | Internal Team | Terminal 2 | Apron | Zone A3 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Replaced dismantled roofing sheet | 5 | 474.94 | m2 | 0.1 | 500 |  | 1 | 0 | 0 | 0 | 23747 | 0 | 0
JCF-203 | Canopy | Roofing System | Dismantled roofing sheet due to Odette or Typhoon "Rai" | Typhoon Odette "Rai" | GMCAC | Internal Team | Terminal 2 | Apron | Zone C1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Replaced dismantled roofing sheet | 5 | 518.69 | m2 | 0.1 | 500 |  | 1 | 0 | 0 | 0 | 25934.5 | 0 | 0
JCF-204 | Canopy | Roofing System | Dismantled roofing sheet due to Odette or Typhoon "Rai" | Typhoon Odette "Rai" | GMCAC | Internal Team | Terminal 2 | Apron | Zone C3 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Replaced dismantled roofing sheet | 3 | 712.12 | m2 | 0.1 | 500 |  | 1 | 0 | 0 | 0 | 35606 | 0 | 0
JCF-205 | Side Walk | Floor System | Ponding of water due to lack of floor drain, drainage and improper sloping | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone D1 | General | Architectural | 2018 | 3 | 3 | 1 | 1 | 2 | Corrective intervention | 3 | 1420.77 | m2 | 0.02 | 1000 |  | 1 | 0 | 0 | 0 | 28415.4 | 0 | 0
JCF-206 | Side Walk | Floor System | Ponding of water due to lack of floor drain, drainage and improper sloping | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone D3 | General | Architectural | 2018 | 3 | 3 | 1 | 1 | 2 | Corrective intervention | 3 | 1417.29 | m2 | 0.02 | 1000 |  | 1 | 0 | 0 | 0 | 28345.8 | 0 | 0
JCF-207 | Side Walk | Floor System | Ponding of water due to lack of floor drain, drainage and improper sloping | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone C1 | General | Architectural | 2018 | 3 | 3 | 1 | 1 | 2 | Corrective intervention | 3 | 518.69 | m2 | 0.1 | 1000 |  | 1 | 0 | 0 | 0 | 51869 | 0 | 0
JCF-208 | Side Walk | Floor System | Ponding of water due to lack of floor drain, drainage and improper sloping | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone C3 | General | Architectural | 2018 | 3 | 3 | 1 | 1 | 2 | Corrective intervention | 3 | 712.12 | m2 | 0.1 | 1000 |  | 1 | 0 | 0 | 0 | 71212 | 0 | 0
JCF-209 | Mesh Ceiling | Ceiling System | Traces of water/liquid leak on the mesh ceiling | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone A4 | General | Architectural | 2018 | 3 | 3 | 1 | 1 | 1 | Cleaning of the affected mesh ceiling and replacement of the piping that causes the leak | 3 | 1439.77 | m2 | 0.02 | 100 |  | 1 | 0 | 0 | 0 | 2879.54 | 0 | 0
JCF-210 | Mesh Ceiling | Ceiling System | Dismantled mesh ceiling that was affected by Odette or Typhoon "Rai" | Typhoon Odette "Rai" | GMCAC | Internal Team | Terminal 2 | Apron | Zone B3 | General | Architectural | 2018 | 2 | 2 | 1 | 1 | 1 | Replaced dismantled roofing sheet | 4 | 1509.96 | m2 | 0.15 | 500 |  | 1 | 0 | 0 | 0 | 113247 | 0 | 0
JCF-211 | Beam | Structural Framing System | Deflection on beam that possibly cause of poor construction | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone A4 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1439.77 | m2 | 0.05 | 2000 |  | 1 | 0 | 0 | 0 | 143977 | 0 | 0
JCF-212 | Floor Tiles | Floor System | There were holes on the floor tiles due to the removal of the luggage cart balustrade | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone C2 | General | Architectural | 2018 | 3 | 3 | 1 | 1 | 1 | Fill in holes or replacement of the affected tile panel | 3 | 1384.87 | m2 | 0.02 | 400 |  | 1 | 0 | 0 | 0 | 11078.96 | 0 | 0
JCF-213 | Floor Tiles | Floor System | There were holes on the floor tiles due to the removal of the luggage cart balustrade | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone C4 | General | Architectural | 2018 | 3 | 3 | 1 | 1 | 1 | Fill in holes or replacement of the affected tile panel | 3 | 1383.23 | m2 | 0.02 | 400 |  | 1 | 0 | 0 | 0 | 11065.84 | 0 | 0
JCF-214 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone A4 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1439.77 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 14397.7 | 0 | 0
JCF-215 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone B3 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1509.96 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 15099.6 | 0 | 0
JCF-216 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone C2 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1384.87 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 13848.7 | 0 | 0
JCF-217 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone C4 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1383.23 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 13832.3 | 0 | 0
JCF-218 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone D1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1420.77 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 14207.7 | 0 | 0
JCF-219 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone D3 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1417.29 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 14172.9 | 0 | 0
JCF-220 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone E1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 260.66 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 2606.6 | 0 | 0
JCF-221 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone E2 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 647.47 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 6474.7 | 0 | 0
JCF-222 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone E3 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 263.84 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 2638.4 | 0 | 0
JCF-223 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone E4 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 697.8 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 6978 | 0 | 0
JCF-224 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone F1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1502.34 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 15023.4 | 0 | 0
JCF-225 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone F2 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1464.13 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 14641.3 | 0 | 0
JCF-226 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone G1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1591.09 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 15910.9 | 0 | 0
JCF-227 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone G2 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 4 | 1594.09 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 15940.9 | 0 | 0
JCF-228 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone H1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 4 | 1128.22 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 11282.2 | 0 | 0
JCF-229 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone H2 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 4 | 1130.82 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 11308.2 | 0 | 0
JCF-230 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone I1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 4 | 756.73 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 7567.3 | 0 | 0
JCF-231 | Elevator | Vertical Transport System | 1) Damage on the metal casing According to the GMCAC this elevator was damage because of the rescue operation made during the time that somebody got trap and the elevator doors are not opening | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone E4 | General | Mechanical | 2018 | 3 | 3 | 2 | 2 | 2 | Repair aluminum sheet casing of the elevator Check and investigate the operating system of the elevator that causes the machine to stop opening | 3 | 697.8 | m2 | 1 | 200 |  | 1 | 0 | 0 | 0 | 139560 | 0 | 0
JCF-232 | Facade Glazing | Curtain Wall System | Glazing panel cracked due to Odette or Typhoon "Rai" | Typhoon Odette "Rai" | GMCAC | Internal Team | Terminal 2 | Arrival | Zone E2 | General | Architectural | 2018 | 5 | 5 | 5 | 5 | 2 | Replacement of broken or damaged façade glazing panel | 6 | 538.88 | m2 | 0.05 | 5000 |  | 1 | 0 | 0 | 0 | 134720 | 0 | 0
JCF-233 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone C2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1396.36 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 209454 | 0 | 0
JCF-234 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone C4 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1394.98 | m2 | 0.2 | 300 |  | 1 | 0 | 0 | 0 | 83698.8 | 0 | 0
JCF-235 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone D1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1402.74 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 210411 | 0 | 0
JCF-236 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone D3 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1385.13 | m2 | 0.2 | 300 |  | 1 | 0 | 0 | 0 | 83107.8 | 0 | 0
JCF-237 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone E2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 538.88 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 80832 | 0 | 0
JCF-238 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone E4 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 618.73 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 92809.5 | 0 | 0
JCF-239 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone F1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1445.4 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 216810 | 0 | 0
JCF-240 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone F2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1463.59 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 219538.5 | 0 | 0
JCF-241 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone F3 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 266.61 | m2 | 1 | 300 |  | 1 | 0 | 0 | 0 | 79983 | 0 | 0
JCF-242 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone F4 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1383.7 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 207555 | 0 | 0
JCF-243 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone G1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1668.32 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 250248 | 0 | 0
JCF-244 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone G2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1480.83 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 222124.5 | 0 | 0
JCF-245 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone G3 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1612.18 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 241827 | 0 | 0
JCF-246 | Suspended Slab | Structural Slab System | Severe crack near Grid Line 11L | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone G3 | General | Structural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1612.18 | m2 | 0.1 | 300 |  | 1 | 0 | 0 | 0 | 48365.4 | 0 | 0
JCF-247 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone H1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1063.65 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 159547.5 | 0 | 0
JCF-248 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone H2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1089.45 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 163417.5 | 0 | 0
JCF-249 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone I1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 727.96 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 109194 | 0 | 0
JCF-250 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone K1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1153.09 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 172963.5 | 0 | 0
JCF-251 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone K3 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 995.26 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 149289 | 0 | 0
JCF-252 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone A2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 416.78 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 83356 | 0 | 0
JCF-253 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone B1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 473.78 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 94756 | 0 | 0
JCF-254 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone A4 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 1092.48 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 218496 | 0 | 0
JCF-255 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone E2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 538.88 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 107776 | 0 | 0
JCF-256 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone E4 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 618.73 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 123746 | 0 | 0
JCF-257 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone F1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 1445.4 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 289080 | 0 | 0
JCF-258 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone F2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 1463.59 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 292718 | 0 | 0
JCF-259 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone G1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 1668.32 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 333664 | 0 | 0
JCF-260 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone G2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 1480.83 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 296166 | 0 | 0
JCF-261 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone H1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 1063.65 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 212730 | 0 | 0
JCF-262 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone H2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 1089.45 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 217890 | 0 | 0
JCF-263 | Beam | Structural Framing System | Poor construction resulting to honeycomb of main lateral resisting frame and exposure of rebar | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone I1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 3 | 727.96 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 145592 | 0 | 0
JCF-264 | Beam | Structural Framing System | Damaged and exposed rebar of beam due to removal of canopy | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone B1 | General | Structural | 2018 | 5 | 5 | 4 | 4 | 3 | Plastering of the structural members that has a exposed rebars and providing epoxy to fill in honeycombs | 5 | 473.78 | m2 | 0.1 | 2000 |  | 1 | 0 | 0 | 0 | 94756 | 0 | 0
JCF-265 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone A4 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1092.48 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 10924.8 | 0 | 0
JCF-266 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone B3 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1117.83 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 11178.3 | 0 | 0
JCF-267 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone C2 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1396.36 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 13963.6 | 0 | 0
JCF-268 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone C4 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1394.98 | m2 | 0.02 | 100 |  | 1 | 0 | 0 | 0 | 2789.96 | 0 | 0
JCF-269 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone D1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1402.74 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 14027.4 | 0 | 0
JCF-270 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone D3 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1385.13 | m2 | 0.02 | 100 |  | 1 | 0 | 0 | 0 | 2770.26 | 0 | 0
JCF-271 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone E1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 236.68 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 2366.8 | 0 | 0
JCF-272 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone E2 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 538.88 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 5388.8 | 0 | 0
JCF-273 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone E3 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 263 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 2630 | 0 | 0
JCF-274 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone E4 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 618.73 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 6187.3 | 0 | 0
JCF-275 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone F1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1445.4 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 14454 | 0 | 0
JCF-276 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone F2 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1463.59 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 14635.9 | 0 | 0
JCF-277 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone G1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1668.32 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 16683.2 | 0 | 0
JCF-278 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone G2 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1480.83 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 14808.3 | 0 | 0
JCF-279 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone H1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1063.65 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 10636.5 | 0 | 0
JCF-280 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone H2 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1089.45 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 10894.5 | 0 | 0
JCF-281 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone I1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 727.96 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 7279.6 | 0 | 0
JCF-282 | Internal Walls | Wall System | Exposed plastic mesh reinforcement of wall due to poor construction | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone G2 | Baggage Handling Area | Architectural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the damaged areas and repainting of walls to cover epoxy patched areas | 3 | 1480.83 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 14808.3 | 0 | 0
JCF-283 | Facade Glazing | Curtain Wall System | Glazings was destroyed by Odette or Typhoon "Rai" | Typhoon Odette "Rai" | GMCAC | Internal Team | Terminal 2 | Departure | Zone A4 | Vestibule | Architectural | 2018 | 5 | 5 | 5 | 5 | 2 | Replacement of broken or damaged façade glazing panel | 5 | 1116.34 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 11163.4 | 0 | 0
JCF-284 | Facade Glazing | Curtain Wall System | Glazings was destroyed by Odette or Typhoon "Rai" | Typhoon Odette "Rai" | GMCAC | Internal Team | Terminal 2 | Departure | Zone B3 | Vestibule | Architectural | 2018 | 5 | 5 | 5 | 5 | 2 | Replacement of broken or damaged façade glazing panel | 5 | 1194.48 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 11944.8 | 0 | 0
JCF-285 | Skylight | Roofing Window System | Glazings was destroyed by Odette or Typhoon "Rai" | Typhoon Odette "Rai" | GMCAC | Internal Team | Terminal 2 | Departure | Zone C2 | Check-in Hall | Architectural | 2018 | 5 | 5 | 5 | 5 | 3 | Replacement of broken or damaged skylight panel | 5 | 1374.41 | m2 | 0.05 | 500 |  | 1 | 0 | 0 | 0 | 34360.25 | 0 | 0
JCF-286 | Skylight | Roofing Window System | Glazings was destroyed by Odette or Typhoon "Rai" | Typhoon Odette "Rai" | GMCAC | Internal Team | Terminal 2 | Departure | Zone C4 | Check-in Hall | Architectural | 2018 | 5 | 5 | 5 | 5 | 3 | Replacement of broken or damaged skylight panel | 5 | 1409.6 | m2 | 0.05 | 500 |  | 1 | 0 | 0 | 0 | 35240 | 0 | 0
JCF-287 | Skylight | Roofing Window System | Glazings was destroyed by Odette or Typhoon "Rai" | Typhoon Odette "Rai" | GMCAC | Internal Team | Terminal 2 | Departure | Zone D1 | Check-in Hall | Architectural | 2018 | 5 | 5 | 5 | 5 | 3 | Replacement of broken or damaged skylight panel | 5 | 1391.84 | m2 | 0.05 | 500 |  | 1 | 0 | 0 | 0 | 34796 | 0 | 0
JCF-288 | Skylight | Roofing Window System | Glazings was destroyed by Odette or Typhoon "Rai" | Typhoon Odette "Rai" | GMCAC | Internal Team | Terminal 2 | Departure | Zone D3 | Check-in Hall | Architectural | 2018 | 5 | 5 | 5 | 5 | 3 | Replacement of broken or damaged skylight panel | 5 | 1393.01 | m2 | 0.05 | 500 |  | 1 | 0 | 0 | 0 | 34825.25 | 0 | 0
JCF-289 | Skylight | Roofing Window System | Glazings was destroyed by Odette or Typhoon "Rai" | Typhoon Odette "Rai" | GMCAC | Internal Team | Terminal 2 | Departure | Zone F2 | Check-in Hall | Architectural | 2018 | 5 | 5 | 5 | 5 | 3 | Replacement of broken or damaged skylight panel | 5 | 1431.02 | m2 | 0.05 | 500 |  | 1 | 0 | 0 | 0 | 35775.5 | 0 | 0
JCF-290 | Skylight | Roofing Window System | Glazings was destroyed by Odette or Typhoon "Rai" | Typhoon Odette "Rai" | GMCAC | Internal Team | Terminal 2 | Departure | Zone F4 | Check-in Hall | Architectural | 2018 | 5 | 5 | 5 | 5 | 3 | Replacement of broken or damaged skylight panel | 5 | 1641.36 | m2 | 0.05 | 500 |  | 1 | 0 | 0 | 0 | 41034 | 0 | 0
JCF-291 | Skylight | Roofing Window System | Glazings was destroyed by Odette or Typhoon "Rai" | Typhoon Odette "Rai" | GMCAC | Internal Team | Terminal 2 | Departure | Zone G1 | Check-in Hall | Architectural | 2018 | 5 | 5 | 5 | 5 | 3 | Replacement of broken or damaged skylight panel | 5 | 1556.69 | m2 | 0.05 | 500 |  | 1 | 0 | 0 | 0 | 38917.25 | 0 | 0
JCF-292 | Skylight | Roofing Window System | Glazings was destroyed by Odette or Typhoon "Rai" | Typhoon Odette "Rai" | GMCAC | Internal Team | Terminal 2 | Departure | Zone G3 | Check-in Hall | Architectural | 2018 | 5 | 5 | 5 | 5 | 3 | Replacement of broken or damaged skylight panel | 5 | 1677.45 | m2 | 0.05 | 500 |  | 1 | 0 | 0 | 0 | 41936.25 | 0 | 0
JCF-293 | Skylight | Roofing Window System | Glazings was destroyed by Odette or Typhoon "Rai" | Typhoon Odette "Rai" | GMCAC | Internal Team | Terminal 2 | Departure | Zone K1 | Check-in Hall | Architectural | 2018 | 5 | 5 | 5 | 5 | 3 | Replacement of broken or damaged skylight panel | 5 | 1091.98 | m2 | 0.05 | 500 |  | 1 | 0 | 0 | 0 | 27299.5 | 0 | 0
JCF-294 | Skylight | Roofing Window System | Glazings was destroyed by Odette or Typhoon "Rai" | Typhoon Odette "Rai" | GMCAC | Internal Team | Terminal 2 | Departure | Zone K3 | Check-in Hall | Architectural | 2018 | 5 | 5 | 5 | 5 | 3 | Replacement of broken or damaged skylight panel | 5 | 1084 | m2 | 0.05 | 500 |  | 1 | 0 | 0 | 0 | 27100 | 0 | 0
JCF-295 | Floor Tiles | Floor System | 1) Floor granite tiles are starting to show discoloration due to ponding of water which is cause of open area with lack of floor drain, drainage and improper sloping for floor 2) Maintenance is expensive due to frequent removal of accumulated water after the rain | Aging | GMCAC | Internal Team | Terminal 2 | Departure | Zone A2 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Treat discolored tiles if still possible. Otherwise, replaced damaged tiles. | 3 | 409.62 | m2 | 1 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 409620
JCF-296 | Floor Tiles | Floor System | 1) Floor granite tiles are starting to show discoloration due to ponding of water which is cause of open area with lack of floor drain, drainage and improper sloping for floor 2) Maintenance is expensive due to frequent removal of accumulated water after the rain | Aging | GMCAC | Internal Team | Terminal 2 | Departure | Zone B1 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Treat discolored tiles if still possible. Otherwise, replaced damaged tiles. | 3 | 455.62 | m2 | 1 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 455620
JCF-297 | Floor Tiles | Floor System | 1) Floor granite tiles are starting to show discoloration due to ponding of water which is cause of open area with lack of floor drain, drainage and improper sloping for floor 2) Maintenance is expensive due to frequent removal of accumulated water after the rain | Aging | GMCAC | Internal Team | Terminal 2 | Departure | Zone A4 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Treat discolored tiles if still possible. Otherwise, replaced damaged tiles. | 3 | 1116.34 | m2 | 0.5 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 558170
JCF-298 | Floor Tiles | Floor System | 1) Floor granite tiles are starting to show discoloration due to ponding of water which is cause of open area with lack of floor drain, drainage and improper sloping for floor 2) Maintenance is expensive due to frequent removal of accumulated water after the rain | Aging | GMCAC | Internal Team | Terminal 2 | Departure | Zone B3 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Treat discolored tiles if still possible. Otherwise, replaced damaged tiles. | 3 | 1194.48 | m2 | 0.5 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 597240
JCF-299 | Ceiling Tiles | Ceiling System | Stains on the ceiling due to water leaks | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone F2 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | 'Replacement of stained ceiling and proper disposal of the existing | 5 | 1431.02 | m2 | 0.1 | 500 |  | 1 | 0 | 0 | 0 | 71551 | 0 | 0
JCF-300 | Ceiling Tiles | Ceiling System | Stains on the ceiling due to water leaks | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone G1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | 'Replacement of stained ceiling and proper disposal of the existing | 5 | 1556.69 | m2 | 0.1 | 500 |  | 1 | 0 | 0 | 0 | 77834.5 | 0 | 0
JCF-301 | Ceiling Tiles | Ceiling System | Stains on the ceiling due to water leaks | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone F4 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | 'Replacement of stained ceiling and proper disposal of the existing | 5 | 1641.36 | m2 | 0.1 | 500 |  | 1 | 0 | 0 | 0 | 82068 | 0 | 0
JCF-302 | Ceiling Tiles | Ceiling System | Stains on the ceiling due to water leaks | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone G3 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | 'Replacement of stained ceiling and proper disposal of the existing | 5 | 1677.45 | m2 | 0.1 | 500 |  | 1 | 0 | 0 | 0 | 83872.5 | 0 | 0
JCF-303 | Ceiling Tiles | Ceiling System | Stains on the ceiling due to water leaks | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone F2 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | 'Replacement of stained ceiling and proper disposal of the existing | 5 | 1463.59 | m2 | 0.1 | 500 |  | 1 | 0 | 0 | 0 | 73179.5 | 0 | 0
JCF-304 | Ceiling Tiles | Ceiling System | Stains on the ceiling due to water leaks | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone G1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | 'Replacement of stained ceiling and proper disposal of the existing | 5 | 1668.32 | m2 | 0.1 | 500 |  | 1 | 0 | 0 | 0 | 83416 | 0 | 0
JCF-305 | Ceiling Tiles | Ceiling System | Stains on the ceiling due to water leaks | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone F4 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | 'Replacement of stained ceiling and proper disposal of the existing | 5 | 1383.7 | m2 | 0.1 | 500 |  | 1 | 0 | 0 | 0 | 69185 | 0 | 0
JCF-306 | Ceiling Tiles | Ceiling System | Stains on the ceiling due to water leaks | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone G3 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | 'Replacement of stained ceiling and proper disposal of the existing | 5 | 1612.18 | m2 | 0.1 | 500 |  | 1 | 0 | 0 | 0 | 80609 | 0 | 0
JCF-307 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone A4 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1092.48 | m2 | 0.3 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 327744
JCF-308 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone B3 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1117.83 | m2 | 0.3 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 335349
JCF-309 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone C2 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1396.36 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 977452
JCF-310 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone D1 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1402.74 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 981918
JCF-311 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone C4 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1394.98 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 976486
JCF-312 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone D3 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1385.13 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 969591
JCF-313 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone E2 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 538.88 | m2 | 0.3 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 161664
JCF-314 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone E4 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 618.73 | m2 | 0.3 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 185619
JCF-315 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone F1 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1445.4 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 1011780
JCF-316 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone F2 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1463.59 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 1024513
JCF-317 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone F4 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1383.7 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 968590
JCF-318 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone G1 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1668.32 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 1167824
JCF-319 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone G2 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1480.83 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 1036581
JCF-320 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone G3 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1612.18 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 1128526
JCF-321 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone H1 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1063.65 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 744555
JCF-322 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone H2 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1089.45 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 762615
JCF-323 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone I1 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 727.96 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 509572
JCF-324 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone K1 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1153.09 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 807163
JCF-325 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | GMCAC | Internal Team | Terminal 2 | Arrival | Zone K3 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 995.26 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 696682
JCF-326 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone A4 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1116.34 | m2 | 0.3 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 334902
JCF-327 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone B3 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1194.48 | m2 | 0.3 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 358344
JCF-328 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone C2 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1374.41 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 962087
JCF-329 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone D1 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1391.84 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 974288
JCF-330 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone C4 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1409.6 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 986720
JCF-331 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone D3 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1393.01 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 975107
JCF-332 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone E2 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 608.56 | m2 | 0.3 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 182568
JCF-333 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone E4 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 667.72 | m2 | 0.3 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 200316
JCF-334 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone F1 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1510.96 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 1057672
JCF-335 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone F2 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1431.02 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 1001714
JCF-336 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone F4 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1641.36 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 1148952
JCF-337 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone G1 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1556.69 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 1089683
JCF-338 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone G2 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1347.9 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 943530
JCF-339 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone G3 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1677.45 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 1174215
JCF-340 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone H1 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1372.29 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 960603
JCF-341 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone H2 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1104.62 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 773234
JCF-342 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone I1 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 758.15 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 530705
JCF-343 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone K1 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1091.98 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 764386
JCF-344 | Terrazo Tiles | Floor System | Hairline cracks on large panel tiles possiibly due to building movement | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone K3 | General | Architectural | 2018 | 3 | 3 | 3 | 3 | 1 | Replacement of tiles will be necessary if cracks progress. | 5 | 1084 | m2 | 0.7 | 1000 |  | 1 | 0 | 0 | 1 | 0 | 0 | 758800
JCF-345 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone C2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1374.41 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 206161.5 | 0 | 0
JCF-346 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone C4 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1409.6 | m2 | 0.2 | 300 |  | 1 | 0 | 0 | 0 | 84576 | 0 | 0
JCF-347 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone D1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1391.84 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 208776 | 0 | 0
JCF-348 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone D3 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1393.01 | m2 | 0.2 | 300 |  | 1 | 0 | 0 | 0 | 83580.6 | 0 | 0
JCF-349 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone E2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 608.56 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 91284 | 0 | 0
JCF-350 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone E4 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 667.72 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 100158 | 0 | 0
JCF-351 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone F1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1510.96 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 226644 | 0 | 0
JCF-352 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone F2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1431.02 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 214653 | 0 | 0
JCF-353 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone F4 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1641.36 | m2 | 1 | 300 |  | 1 | 0 | 0 | 0 | 492408 | 0 | 0
JCF-354 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone F4 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1641.36 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 246204 | 0 | 0
JCF-355 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone G1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1556.69 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 233503.5 | 0 | 0
JCF-356 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone G2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1347.9 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 202185 | 0 | 0
JCF-357 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone G3 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1677.45 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 251617.5 | 0 | 0
JCF-358 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone H1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1372.29 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 205843.5 | 0 | 0
JCF-359 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone H2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1104.62 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 165693 | 0 | 0
JCF-360 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone I1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 758.15 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 113722.5 | 0 | 0
JCF-361 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone K1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1091.98 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 163797 | 0 | 0
JCF-362 | Suspended Slab | Structural Slab System | Hairline cracks and honeycomb on suspended slab | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone K3 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Apply epoxy to fill in the visible slab cracks | 3 | 1084 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 162600 | 0 | 0
JCF-363 | Timber Roof Main Support | Structural Framing System | Timber supports of the roof starting to show expansions on its grains resulted to cracks possibly due to movement of the structure especially during the Typhoon Odette | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone E2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Conduct structural evaluation to comply with the current structural code of the philippines May undergo retrofitting to mitigate the progression of the cracks | 4 | 608.56 | m2 | 0.15 | 6000 |  | 1 | 0 | 0 | 0 | 547704 | 0 | 0
JCF-364 | Timber Roof Main Support | Structural Framing System | Timber supports of the roof starting to show expansions on its grains resulted to cracks possibly due to movement of the structure especially during the Typhoon Odette | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone E4 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Conduct structural evaluation to comply with the current structural code of the philippines May undergo retrofitting to mitigate the progression of the cracks | 4 | 667.72 | m2 | 0.15 | 6000 |  | 1 | 0 | 0 | 0 | 600948 | 0 | 0
JCF-365 | Timber Roof Main Support | Structural Framing System | Timber supports of the roof starting to show expansions on its grains resulted to cracks possibly due to movement of the structure especially during the Typhoon Odette | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone F1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Conduct structural evaluation to comply with the current structural code of the philippines May undergo retrofitting to mitigate the progression of the cracks | 4 | 1510.96 | m2 | 0.15 | 6000 |  | 1 | 0 | 0 | 0 | 1359864 | 0 | 0
JCF-366 | Timber Roof Main Support | Structural Framing System | Timber supports of the roof starting to show expansions on its grains resulted to cracks possibly due to movement of the structure especially during the Typhoon Odette | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone F2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Conduct structural evaluation to comply with the current structural code of the philippines May undergo retrofitting to mitigate the progression of the cracks | 4 | 1431.02 | m2 | 0.15 | 6000 |  | 1 | 0 | 0 | 0 | 1287918 | 0 | 0
JCF-367 | Timber Roof Main Support | Structural Framing System | Timber supports of the roof starting to show expansions on its grains resulted to cracks possibly due to movement of the structure especially during the Typhoon Odette | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone F4 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Conduct structural evaluation to comply with the current structural code of the philippines May undergo retrofitting to mitigate the progression of the cracks | 4 | 1641.36 | m2 | 0.15 | 6000 |  | 1 | 0 | 0 | 0 | 1477224 | 0 | 0
JCF-368 | Timber Roof Main Support | Structural Framing System | Timber supports of the roof starting to show expansions on its grains resulted to cracks possibly due to movement of the structure especially during the Typhoon Odette | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone G1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Conduct structural evaluation to comply with the current structural code of the philippines May undergo retrofitting to mitigate the progression of the cracks | 4 | 1556.69 | m2 | 0.15 | 6000 |  | 1 | 0 | 0 | 0 | 1401021 | 0 | 0
JCF-369 | Timber Roof Main Support | Structural Framing System | Timber supports of the roof starting to show expansions on its grains resulted to cracks possibly due to movement of the structure especially during the Typhoon Odette | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone G2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Conduct structural evaluation to comply with the current structural code of the philippines May undergo retrofitting to mitigate the progression of the cracks | 4 | 1347.9 | m2 | 0.15 | 6000 |  | 1 | 0 | 0 | 0 | 1213110 | 0 | 0
JCF-370 | Timber Roof Main Support | Structural Framing System | Timber supports of the roof starting to show expansions on its grains resulted to cracks possibly due to movement of the structure especially during the Typhoon Odette | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone G3 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Conduct structural evaluation to comply with the current structural code of the philippines May undergo retrofitting to mitigate the progression of the cracks | 4 | 1677.45 | m2 | 0.15 | 6000 |  | 1 | 0 | 0 | 0 | 1509705 | 0 | 0
JCF-371 | Timber Roof Main Support | Structural Framing System | Timber supports of the roof starting to show expansions on its grains resulted to cracks possibly due to movement of the structure especially during the Typhoon Odette | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone H1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Conduct structural evaluation to comply with the current structural code of the philippines May undergo retrofitting to mitigate the progression of the cracks | 4 | 1372.29 | m2 | 0.15 | 6000 |  | 1 | 0 | 0 | 0 | 1235061 | 0 | 0
JCF-372 | Timber Roof Main Support | Structural Framing System | Timber supports of the roof starting to show expansions on its grains resulted to cracks possibly due to movement of the structure especially during the Typhoon Odette | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone H2 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Conduct structural evaluation to comply with the current structural code of the philippines May undergo retrofitting to mitigate the progression of the cracks | 4 | 1104.62 | m2 | 0.15 | 6000 |  | 1 | 0 | 0 | 0 | 994158 | 0 | 0
JCF-373 | Timber Roof Main Support | Structural Framing System | Timber supports of the roof starting to show expansions on its grains resulted to cracks possibly due to movement of the structure especially during the Typhoon Odette | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone I1 | General | Structural | 2018 | 3 | 3 | 2 | 2 | 1 | Conduct structural evaluation to comply with the current structural code of the philippines May undergo retrofitting to mitigate the progression of the cracks | 4 | 758.15 | m2 | 0.15 | 6000 |  | 1 | 0 | 0 | 0 | 682335 | 0 | 0
JCF-374 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone A4 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1116.34 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 11163.4 | 0 | 0
JCF-375 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone B3 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1194.48 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 11944.8 | 0 | 0
JCF-376 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone C2 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1374.41 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 13744.1 | 0 | 0
JCF-377 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone C4 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1409.6 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 14096 | 0 | 0
JCF-378 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone D1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1391.84 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 13918.4 | 0 | 0
JCF-379 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone D3 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1393.01 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 13930.1 | 0 | 0
JCF-380 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone E1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 232.62 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 2326.2 | 0 | 0
JCF-381 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone E2 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 608.56 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 6085.6 | 0 | 0
JCF-382 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone E3 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 261.19 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 2611.9 | 0 | 0
JCF-383 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone E4 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 667.72 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 6677.2 | 0 | 0
JCF-384 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone F1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1510.96 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 15109.6 | 0 | 0
JCF-385 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone F2 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1431.02 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 14310.2 | 0 | 0
JCF-386 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone G1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1556.69 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 15566.9 | 0 | 0
JCF-387 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone G2 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1347.9 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 13479 | 0 | 0
JCF-388 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone H1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1372.29 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 13722.9 | 0 | 0
JCF-389 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone H2 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 1104.62 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 11046.2 | 0 | 0
JCF-390 | Internal Walls | Wall System | Hairline cracks on wall, especially those walls directly below the beams and near the elevator shafts | Damage | GMCAC | Internal Team | Terminal 2 | Departure | Zone I1 | General | Architectural | 2018 | 4 | 4 | 3 | 3 | 1 | Apply epoxy to fill in the wall cracks and repainting of walls to cover epoxy patched areas | 3 | 758.15 | m2 | 0.1 | 100 |  | 1 | 0 | 0 | 0 | 7581.5 | 0 | 0
JCF-391 | Pipe | Equipment and Machinery Supports | no lateral support between two (2) floors | Others | GMCAC | Internal Team | Terminal 2 | Arrival | Zone G1 | Lobby | Structural | 2018 | 2 | 2 | 2 | 2 | 1 | Provide lateral supports | 3 | 1668.32 | m2 | 0.01 | 80 |  | 1 | 0 | 0 | 0 | 1334.656 | 0 | 0
JCF-392 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone F1 | Baggage Handling Area | Civil | 2018 | 3 | 3 | 3 | 3 | 2 | Crack sealing | 3 | 1502.34 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 60093.6 | 0 | 0
JCF-393 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone F2 | Baggage Handling Area | Civil | 2018 | 3 | 3 | 3 | 3 | 2 | Crack sealing | 3 | 1464.13 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 58565.2 | 0 | 0
JCF-394 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone G1 | Baggage Handling Area | Civil | 2018 | 3 | 3 | 3 | 3 | 2 | Crack sealing | 3 | 1591.09 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 63643.6 | 0 | 0
JCF-395 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone G2 | Baggage Handling Area | Civil | 2018 | 3 | 3 | 3 | 3 | 2 | Crack sealing | 3 | 1594.09 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 63763.6 | 0 | 0
JCF-396 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone H1 | Baggage Handling Area | Civil | 2018 | 3 | 3 | 3 | 3 | 2 | Crack sealing | 3 | 1128.22 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 45128.8 | 0 | 0
JCF-397 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone H2 | Baggage Handling Area | Civil | 2018 | 3 | 3 | 3 | 3 | 2 | Crack sealing | 3 | 1130.82 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 45232.8 | 0 | 0
JCF-398 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | GMCAC | Internal Team | Terminal 2 | Apron | Zone I1 | Baggage Handling Area | Civil | 2018 | 3 | 3 | 3 | 3 | 2 | Crack sealing | 3 | 756.73 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 30269.2 | 0 | 0
JCF-399 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | GMCAC | Internal Team | Airside | Outside Terminal | AP111 | General | Civil | 1994 | 3 | 3 | 3 | 3 | 2 | Crack sealing | 3 | 10800 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 432000 | 0 | 0
JCF-400 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | GMCAC | Internal Team | Airside | Outside Terminal | AP112 | General | Civil | 1994 | 3 | 3 | 3 | 3 | 2 | Crack sealing | 3 | 10800 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 432000 | 0 | 0
JCF-401 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | GMCAC | Internal Team | Airside | Outside Terminal | AP113 | General | Civil | 1994 | 3 | 3 | 3 | 3 | 2 | Crack sealing | 3 | 8100 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 324000 | 0 | 0
JCF-402 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | GMCAC | Internal Team | Airside | Outside Terminal | AP114 | General | Civil | 1994 | 3 | 3 | 3 | 3 | 2 | Crack sealing | 3 | 8100 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 324000 | 0 | 0
JCF-403 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | GMCAC | Internal Team | Airside | Outside Terminal | AP115 | General | Civil | 1994 | 3 | 3 | 3 | 3 | 2 | Crack sealing | 3 | 8100 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 324000 | 0 | 0
JCF-404 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | GMCAC | Internal Team | Airside | Outside Terminal | AP116 | General | Civil | 1994 | 3 | 3 | 3 | 3 | 2 | Crack sealing | 3 | 8100 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 324000 | 0 | 0
JCF-405 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks 2) Ponding of water possibly due to uneven surface | Damage | GMCAC | Internal Team | Airside | Outside Terminal | AP117 | General | Civil | 1994 | 3 | 3 | 3 | 3 | 2 | Repair the cracked areas with epoxy injection and level area to suite the design slope of the apron pavement | 3 | 8100 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 324000 | 0 | 0
JCF-406 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | GMCAC | Internal Team | Airside | Outside Terminal | AP118 | General | Civil | 1994 | 3 | 3 | 3 | 3 | 2 | Crack sealing | 3 | 8100 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 324000 | 0 | 0
JCF-407 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | GMCAC | Internal Team | Airside | Outside Terminal | AP119 | General | Civil | 1994 | 3 | 3 | 3 | 3 | 2 | Crack sealing | 3 | 8100 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 324000 | 0 | 0
JCF-408 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | GMCAC | Internal Team | Airside | Outside Terminal | AP120 | General | Civil | 1994 | 3 | 3 | 3 | 3 | 2 | Crack sealing | 3 | 8100 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 324000 | 0 | 0
JCF-409 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | GMCAC | Internal Team | Airside | Outside Terminal | AP121 | General | Civil | 1994 | 3 | 3 | 3 | 3 | 2 | Crack sealing | 3 | 8100 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 324000 | 0 | 0
JCF-410 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | GMCAC | Internal Team | Airside | Outside Terminal | AP122 | General | Civil | 1994 | 3 | 3 | 3 | 3 | 2 | Crack sealing | 3 | 8100 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 324000 | 0 | 0
JCF-411 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | GMCAC | Internal Team | Airside | Outside Terminal | AP123 | General | Civil | 1994 | 3 | 3 | 3 | 3 | 2 | Crack sealing | 3 | 13500 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 540000 | 0 | 0
JCF-412 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | GMCAC | Internal Team | Airside | Outside Terminal | AP124 | General | Civil | 1994 | 3 | 3 | 3 | 3 | 2 | Crack sealing | 3 | 13500 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 540000 | 0 | 0
JCF-413 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks 2) Ponding of water possibly due to uneven surface | Damage | GMCAC | Internal Team | Airside | Outside Terminal | AP211 | General | Civil | 2018 | 3 | 3 | 1 | 1 | 1 | Repair the cracked areas with epoxy injection and level area to suite the design slope of the apron pavement | 3 | 8100 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 324000 | 0 | 0
JCF-414 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks 2) Ponding of water possibly due to uneven surface | Damage | GMCAC | Internal Team | Airside | Outside Terminal | AP212 | General | Civil | 2018 | 3 | 3 | 1 | 1 | 1 | Repair the cracked areas with epoxy injection and level area to suite the design slope of the apron pavement | 3 | 8100 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 324000 | 0 | 0
JCF-415 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface | Construction Issue | GMCAC | Internal Team | Airside | Outside Terminal | AP213 | General | Civil | 2018 | 3 | 3 | 1 | 1 | 1 | Level area to suite the design slope of the apron pavement | 3 | 8100 | m2 | 0.03 | 1500 |  | 1 | 0 | 1 | 0 | 0 | 364500 | 0
JCF-416 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface | Construction Issue | GMCAC | Internal Team | Airside | Outside Terminal | AP214 | General | Civil | 2018 | 3 | 3 | 1 | 1 | 1 | Level area to suite the design slope of the apron pavement | 3 | 8100 | m2 | 0.03 | 1500 |  | 1 | 0 | 1 | 0 | 0 | 364500 | 0
JCF-417 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks | Damage | GMCAC | Internal Team | Airside | Outside Terminal | AP215 | General | Civil | 2018 | 3 | 3 | 1 | 1 | 1 | Repair the cracked areas with epoxy injection | 3 | 8100 | m2 | 0.2 | 200 |  | 1 | 0 | 0 | 0 | 324000 | 0 | 0
JCF-418 | Pavement | Road and Parking Surface System | 1) Longitudinal and Transverse Cracks 2) Ponding of water possibly due to uneven surface | Damage | GMCAC | Internal Team | Airside | Outside Terminal | AP216 | General | Civil | 2018 | 3 | 3 | 1 | 1 | 1 | Repair the cracked areas with epoxy injection and level area to suite the design slope of the apron pavement | 3 | 8100 | m2 | 0.03 | 1500 |  | 1 | 0 | 1 | 0 | 0 | 364500 | 0
JCF-419 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface | Construction Issue | GMCAC | Internal Team | Airside | Outside Terminal | AP217 | General | Civil | 2018 | 3 | 3 | 1 | 1 | 1 | Leveling | 3 | 8100 | m2 | 0.03 | 1500 |  | 1 | 0 | 0 | 0 | 364500 | 0 | 0
JCF-420 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface | Construction Issue | GMCAC | Internal Team | Airside | Outside Terminal | AP218 | General | Civil | 2018 | 3 | 3 | 1 | 1 | 1 | Leveling | 3 | 8100 | m2 | 0.03 | 1500 |  | 1 | 0 | 0 | 0 | 364500 | 0 | 0
JCF-421 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface | Construction Issue | GMCAC | Internal Team | Airside | Outside Terminal | AP219 | General | Civil | 2018 | 3 | 3 | 1 | 1 | 1 | Leveling | 3 | 8100 | m2 | 0.03 | 1500 |  | 1 | 0 | 0 | 0 | 364500 | 0 | 0
JCF-422 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface | Construction Issue | GMCAC | Internal Team | Airside | Outside Terminal | AP220 | General | Civil | 2018 | 3 | 3 | 1 | 1 | 1 | Leveling | 3 | 8100 | m2 | 0.03 | 1500 |  | 1 | 0 | 0 | 0 | 364500 | 0 | 0
JCF-423 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface | Construction Issue | GMCAC | Internal Team | Airside | Outside Terminal | AP221 | General | Civil | 2018 | 3 | 3 | 1 | 1 | 1 | Leveling | 3 | 8100 | m2 | 0.03 | 1500 |  | 1 | 0 | 0 | 0 | 364500 | 0 | 0
JCF-424 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface | Construction Issue | GMCAC | Internal Team | Airside | Outside Terminal | AP222 | General | Civil | 2018 | 3 | 3 | 1 | 1 | 1 | Leveling | 3 | 8100 | m2 | 0.03 | 1500 |  | 1 | 0 | 0 | 0 | 364500 | 0 | 0
JCF-425 | Louver | Louvers and Vent | Missing louver pannel due to Odette or Typhoon "Rai" | Typhoon Odette "Rai" | GMCAC | Internal Team | Landside | Outside Terminal | R1003 | General | Civil | 2018 | 3 | 3 | 2 | 2 | 1 | Replacement of detached louvers | 5 | 3555 | m2 | 0.5 | 300 |  | 1 | 0 | 0 | 0 | 533250 | 0 | 0
JCF-426 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface and lack of drainage | Construction Issue | GMCAC | Internal Team | Landside | Outside Terminal | R1011 | General | Civil | 2018 | 3 | 3 | 2 | 2 | 1 | Level area to suite the design slope of the pavement | 3 | 1110 | m2 | 0.3 | 2000 |  | 1 | 0 | 0 | 0 | 666000 | 0 | 0
JCF-427 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface and lack of drainage | Construction Issue | GMCAC | Internal Team | Landside | Outside Terminal | R1012 | General | Civil | 2018 | 3 | 3 | 2 | 2 | 1 | Level area to suite the design slope of the pavement | 3 | 840 | m2 | 0.3 | 2000 |  | 1 | 0 | 0 | 0 | 504000 | 0 | 0
JCF-428 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface and lack of drainage | Construction Issue | GMCAC | Internal Team | Landside | Outside Terminal | R1013 | General | Civil | 2018 | 3 | 3 | 2 | 2 | 1 | Level area to suite the design slope of the pavement | 3 | 350 | m2 | 0.3 | 2000 |  | 1 | 0 | 0 | 0 | 210000 | 0 | 0
JCF-429 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface and lack of drainage | Construction Issue | GMCAC | Internal Team | Landside | Outside Terminal | R1014 | General | Civil | 2018 | 3 | 3 | 2 | 2 | 1 | Level area to suite the design slope of the pavement | 3 | 880 | m2 | 0.3 | 2000 |  | 1 | 0 | 0 | 0 | 528000 | 0 | 0
JCF-430 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface and lack of drainage | Construction Issue | GMCAC | Internal Team | Landside | Outside Terminal | P101 | General | Civil | 2018 | 3 | 3 | 2 | 2 | 1 | Level area to suite the design slope of the pavement | 3 | 810 | m2 | 0.3 | 2000 |  | 1 | 0 | 0 | 0 | 486000 | 0 | 0
JCF-431 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface and lack of drainage | Construction Issue | GMCAC | Internal Team | Landside | Outside Terminal | P105 | General | Civil | 2018 | 3 | 3 | 2 | 2 | 1 | Level area to suite the design slope of the pavement | 3 | 810 | m2 | 0.3 | 2000 |  | 1 | 0 | 0 | 0 | 486000 | 0 | 0
JCF-432 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface and lack of drainage | Construction Issue | GMCAC | Internal Team | Landside | Outside Terminal | P109 | General | Civil | 2018 | 3 | 3 | 2 | 2 | 1 | Level area to suite the design slope of the pavement | 3 | 810 | m2 | 0.3 | 2000 |  | 1 | 0 | 0 | 0 | 486000 | 0 | 0
JCF-433 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface and lack of drainage | Construction Issue | GMCAC | Internal Team | Landside | Outside Terminal | P113 | General | Civil | 2018 | 3 | 3 | 2 | 2 | 1 | Level area to suite the design slope of the pavement | 3 | 810 | m2 | 0.3 | 2000 |  | 1 | 0 | 0 | 0 | 486000 | 0 | 0
JCF-434 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface and lack of drainage | Construction Issue | GMCAC | Internal Team | Landside | Outside Terminal | P117 | General | Civil | 2018 | 3 | 3 | 2 | 2 | 1 | Level area to suite the design slope of the pavement | 3 | 810 | m2 | 0.3 | 2000 |  | 1 | 0 | 0 | 0 | 486000 | 0 | 0
JCF-435 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface and lack of drainage | Construction Issue | GMCAC | Internal Team | Landside | Outside Terminal | P120 | General | Civil | 2018 | 3 | 3 | 2 | 2 | 1 | Level area to suite the design slope of the pavement | 3 | 810 | m2 | 0.3 | 2000 |  | 1 | 0 | 0 | 0 | 486000 | 0 | 0
JCF-436 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface and lack of drainage | Construction Issue | GMCAC | Internal Team | Landside | Outside Terminal | P121 | General | Civil | 2018 | 3 | 3 | 2 | 2 | 1 | Level area to suite the design slope of the pavement | 3 | 810 | m2 | 0.3 | 2000 |  | 1 | 0 | 0 | 0 | 486000 | 0 | 0
JCF-437 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface and lack of drainage | Construction Issue | GMCAC | Internal Team | Landside | Outside Terminal | P122 | General | Civil | 2018 | 3 | 3 | 2 | 2 | 1 | Level area to suite the design slope of the pavement | 3 | 810 | m2 | 0.3 | 2000 |  | 1 | 0 | 0 | 0 | 486000 | 0 | 0
JCF-438 | Pavement | Road and Parking Surface System | Ponding of water possibly due to uneven surface and lack of drainage | Construction Issue | GMCAC | Internal Team | Landside | Outside Terminal | P123 | General | Civil | 2018 | 3 | 3 | 2 | 2 | 1 | Level area to suite the design slope of the pavement | 3 | 810 | m2 | 0.3 | 2000 |  | 1 | 0 | 0 | 0 | 486000 | 0 | 0
JCF-439 | Metal Roof | Roofing System | Damaged roofing due to Odette or Typhoon "Rai" | Typhoon Odette "Rai" | GMCAC | Internal Team | Landside | Outside Terminal | T122 | General | Architectural | 2018 | 5 | 5 | 5 | 5 | 2 | Replacement | 5 | 395 | m2 | 0.6 | 1000 |  | 1 | 0 | 0 | 0 | 237000 | 0 | 0
JCF-440 | Metal Roof | Roofing System | Damaged roofing due to Odette or Typhoon "Rai" | Typhoon Odette "Rai" | GMCAC | Internal Team | Landside | Outside Terminal | T123 | General | Architectural | 2018 | 5 | 5 | 5 | 5 | 2 | Replacement | 5 | 395 | m2 | 0.6 | 1000 |  | 1 | 0 | 0 | 0 | 237000 | 0 | 0
JCF-441 | Metal Roof | Roofing System | Damaged roofing due to Odette or Typhoon "Rai" | Typhoon Odette "Rai" | GMCAC | Internal Team | Landside | Outside Terminal | T126 | General | Architectural | 2018 | 5 | 5 | 5 | 5 | 2 | Replacement | 5 | 395 | m2 | 0.2 | 1000 |  | 1 | 0 | 0 | 0 | 79000 | 0 | 0
JCF-442 | Metal Roof | Roofing System | Damaged roofing due to Odette or Typhoon "Rai" | Typhoon Odette "Rai" | GMCAC | Internal Team | Terminal 2 | Roof Level | Zone I1 | General | Architectural | 2018 | 5 | 5 | 5 | 5 | 2 | Replaced damaged roofing sheet | 5 | 758.15 | m2 | 0.1 | 1000 |  | 1 | 0 | 0 | 0 | 75815 | 0 | 0
JCF-443 | Metal Roof | Roofing System | Damaged roofing due to Odette or Typhoon "Rai" | Typhoon Odette "Rai" | GMCAC | Internal Team | Terminal 2 | Roof Level | Zone G2 | General | Architectural | 2018 | 5 | 5 | 5 | 5 | 2 | Replaced damaged roofing sheet | 5 | 1347.9 | m2 | 0.1 | 1000 |  | 1 | 0 | 0 | 0 | 134790 | 0 | 0
JCF-444 | Metal Roof | Roofing System | Damaged roofing due to Odette or Typhoon "Rai" | Typhoon Odette "Rai" | GMCAC | Internal Team | Terminal 2 | Roof Level | Zone K1 | General | Architectural | 2018 | 5 | 5 | 5 | 5 | 2 | Replaced damaged roofing sheet | 5 | 1091.98 | m2 | 0.1 | 1000 |  | 1 | 0 | 0 | 0 | 109198 | 0 | 0
Note on X106: +5000 if structural members is included
Note on A241: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Federizo, Joseph

## Cause
Typhoon Odette "Rai"
Damage
Construction Issue
Aging

## Operators
GMCAC
MCIAA
`

## Vendors
Third Party
Internal Team
Government
`

## Systems
Standby Generator System | Electrical
Low Voltage Distribution | Electrical
General Lighting and Power System | Electrical
Earthing and Lightning System | Electrical
Photovoltaic System | Electrical
Structural Framing System | Structural
Roofing System | Architectural
Floor System | Architectural
Ceiling System | Architectural
Curtain Wall System | Architectural
Wall System | Architectural
Doors and Accessories | Architectural
Louvers and Vent | Architectural
Vegetation | Architectural
Fire Protection System | Fire
Plumbing System | Plumbing
Road and Parking Surface System | Civil | `
Equipment and Machinery Supports | Structural
Architectural Elements Supports | Structural
Vertical Transport System | Mechanical
Structural Slab System | Structural
Roofing Window System | Architectural
MVAC System | Mechanical
STP System | Environmental
Roof Structural Framing System | Structural

## Area
Terminal 1
Terminal 2
Airside
Landside
General

## Level
Apron
Arrival
Departure
Roof Level
Basement
Outside Terminal
General

## Zone
Zone A1
Zone A2
Zone A3
Zone A4
Zone B1
Zone B2
Zone B3
Zone B4
Zone C1
Zone C2
Zone C3
Zone C4
Zone D1
Zone D2
Zone D3
Zone D4
Zone E1
Zone E2
Zone E3
Zone E4
Zone F1
Zone F2
Zone F3
Zone F4
Zone G1
Zone G2
Zone G3
Zone G4
Zone H1
Zone H2
Zone H3
Zone H4
Zone I1
Zone I2
Zone I3
Zone I4
Zone J1
Zone J2
Zone J3
Zone J4
Zone K1
Zone K2
Zone K3
Zone K4
All Zone
All Other Zones
General
AP111 | Apron
AP112 | Apron
AP113 | Apron
AP114 | Apron
AP115 | Apron
AP116 | Apron
AP117 | Apron
AP118 | Apron
AP119 | Apron
AP120 | Apron
AP121 | Apron
AP122 | Apron
AP123 | Apron
AP124 | Apron
AP211 | Apron
AP212 | Apron
AP213 | Apron
AP214 | Apron
AP215 | Apron
AP216 | Apron
AP217 | Apron
AP218 | Apron
AP219 | Apron
AP220 | Apron
AP221 | Apron
AP222 | Apron
R1001 | Road
R1002 | Road
R1003 | Road
R1004 | Road
R1005 | Road
R1006 | Road
R1007 | Road
R1008 | Road
R1009 | Road
R1010 | Road
R1011 | Road
R1012 | Road
R1013 | Road
R1014 | Road
P101 | Parking
P102 | Parking
P103 | Parking
P104 | Parking
P105 | Parking
P106 | Parking
P107 | Parking
P108 | Parking
P109 | Parking
P110 | Parking
P111 | Parking
P112 | Parking
P113 | Parking
P114 | Parking
P115 | Parking
P116 | Parking
P117 | Parking
P118 | Parking
P119 | Parking
P120 | Parking
P121 | Parking
P122 | Parking
P123 | Parking
P124 | Parking
T101 | Transport Hub
T102 | Transport Hub
T103 | Transport Hub
T104 | Transport Hub
T105 | Transport Hub
T106 | Transport Hub
T107 | Transport Hub
T108 | Transport Hub
T109 | Transport Hub
T110 | Transport Hub
T111 | Transport Hub
T112 | Transport Hub
T113 | Transport Hub
T114 | Transport Hub
T115 | Transport Hub
T116 | Transport Hub
T117 | Transport Hub
T118 | Transport Hub
T119 | Transport Hub
T120 | Transport Hub
T121 | Transport Hub
T122 | Transport Hub
T123 | Transport Hub
T124 | Transport Hub
T125 | Transport Hub
T126 | Transport Hub
T127 | Transport Hub
T128 | Transport Hub
T129 | Transport Hub
T130 | Transport Hub
T131 | Transport Hub
T132 | Transport Hub
T133 | Transport Hub
T134 | Transport Hub
T135 | Transport Hub
T136 | Transport Hub
S101 | Runway & Taxiway
S102 | Runway & Taxiway
S103 | Runway & Taxiway
S104 | Runway & Taxiway
S105 | Runway & Taxiway
S106 | Runway & Taxiway
S107 | Runway & Taxiway
S108 | Runway & Taxiway
S109 | Runway & Taxiway
S110 | Runway & Taxiway
S111 | Runway & Taxiway
S112 | Runway & Taxiway
S113 | Runway & Taxiway
S114 | Runway & Taxiway
S115 | Runway & Taxiway
S116 | Runway & Taxiway
S117 | Runway & Taxiway
S118 | Runway & Taxiway
S119 | Runway & Taxiway
S120 | Runway & Taxiway
S121 | Runway & Taxiway
S122 | Runway & Taxiway
S123 | Runway & Taxiway
S124 | Runway & Taxiway
S125 | Runway & Taxiway
S126 | Runway & Taxiway
S127 | Runway & Taxiway
S128 | Runway & Taxiway
S129 | Runway & Taxiway
S130 | Runway & Taxiway
S131 | Runway & Taxiway
S132 | Runway & Taxiway
S133 | Runway & Taxiway
S134 | Runway & Taxiway
S135 | Runway & Taxiway
S136 | Runway & Taxiway
S137 | Runway & Taxiway
S138 | Runway & Taxiway
S139 | Runway & Taxiway
S140 | Runway & Taxiway
S141 | Runway & Taxiway
S142 | Runway & Taxiway
S143 | Runway & Taxiway
S144 | Runway & Taxiway
S145 | Runway & Taxiway
S146 | Runway & Taxiway
S147 | Runway & Taxiway
S148 | Runway & Taxiway
S149 | Runway & Taxiway
S150 | Runway & Taxiway

## AreaQty
Area | Level | Zone | Zone | Area Quantity
Terminal 1 | Arrival | A1 | Zone A1 | 620.26
Terminal 1 | Arrival | A2 | Zone A2 | 756.84
Terminal 1 | Arrival | A2 | Zone A2 | 197.77
Terminal 1 | Arrival | A4 | Zone A4 | 274.87
Terminal 1 | Arrival | B1 | Zone B1 | 1146.19
Terminal 1 | Arrival | B2 | Zone B2 | 978.22
Terminal 1 | Arrival | B3 | Zone B3 | 1389.9
Terminal 1 | Arrival | B4 | Zone B4 | 1157.59
Terminal 1 | Arrival | C1 | Zone C1 | 1128.74
Terminal 1 | Arrival | C2 | Zone C2 | 1000.72
Terminal 1 | Arrival | C3 | Zone C3 | 1390.72
Terminal 1 | Arrival | C4 | Zone C4 | 1157.87
Terminal 1 | Arrival | D1 | Zone D1 | 1250.95
Terminal 1 | Arrival | D2 | Zone D2 | 1054.2
Terminal 1 | Arrival | D3 | Zone D3 | 1389.08
Terminal 1 | Arrival | D4 | Zone D4 | 159.05
Terminal 1 | Arrival | D4 | Zone D4 | 140.97
Terminal 1 | Arrival | D4 | Zone D4 | 9.03
Terminal 1 | Arrival | E1 | Zone E1 | 1356.4
Terminal 1 | Arrival | E2 | Zone E2 | 1705.18
Terminal 1 | Arrival | E3 | Zone E3 | 269.83
Terminal 1 | Arrival | E4 | Zone E4 | 350.43
Terminal 1 | Arrival | F1 | Zone F1 | 1705.04
Terminal 1 | Arrival | F2 | Zone F2 | 1321.57
Terminal 1 | Arrival | F3 | Zone F3 | 351.12
Terminal 1 | Arrival | F4 | Zone F4 | 308.16
Terminal 1 | Departure | A1 | Zone A1 | 445.65
Terminal 1 | Departure | A2 | Zone A2 | 883.93
Terminal 1 | Departure | A4 | Zone A4 | 305.84
Terminal 1 | Departure | B1 | Zone B1 | 1064.43
Terminal 1 | Departure | B2 | Zone B2 | 913.85
Terminal 1 | Departure | B3 | Zone B3 | 1383.54
Terminal 1 | Departure | B4 | Zone B4 | 1154.06
Terminal 1 | Departure | C1 | Zone C1 | 1113.7
Terminal 1 | Departure | C2 | Zone C2 | 992.1
Terminal 1 | Departure | C3 | Zone C3 | 1382.79
Terminal 1 | Departure | C4 | Zone C4 | 1155.58
Terminal 1 | Departure | D1 | Zone D1 | 1215.21
Terminal 1 | Departure | D2 | Zone D2 | 1016.77
Terminal 1 | Departure | D3 | Zone D3 | 1383.41
Terminal 1 | Departure | D4 | Zone D4 | 484.55
Terminal 1 | Departure | E1 | Zone E1 | 1431.54
Terminal 1 | Departure | E2 | Zone E2 | 1697.69
Terminal 1 | Departure | E3 | Zone E3 | 1149.15
Terminal 1 | Departure | E4 | Zone E4 | 1575.71
Terminal 1 | Departure | F1 | Zone F1 | 1700.03
Terminal 1 | Departure | F2 | Zone F2 | 1428.08
Terminal 1 | Departure | F3 | Zone F3 | 1575.04
Terminal 1 | Departure | F4 | Zone F4 | 1186.65
Terminal 1 | Roof Level | A1 | Zone A1 | 445.65
Terminal 1 | Roof Level | A2 | Zone A2 | 883.93
Terminal 1 | Roof Level | A4 | Zone A4 | 305.84
Terminal 1 | Roof Level | B1 | Zone B1 | 1064.43
Terminal 1 | Roof Level | B2 | Zone B2 | 913.85
Terminal 1 | Roof Level | B3 | Zone B3 | 1383.54
Terminal 1 | Roof Level | B4 | Zone B4 | 1154.06
Terminal 1 | Roof Level | C1 | Zone C1 | 1113.7
Terminal 1 | Roof Level | C2 | Zone C2 | 992.1
Terminal 1 | Roof Level | C3 | Zone C3 | 1382.79
Terminal 1 | Roof Level | C4 | Zone C4 | 1155.58
Terminal 1 | Roof Level | D1 | Zone D1 | 1215.21
Terminal 1 | Roof Level | D2 | Zone D2 | 1016.77
Terminal 1 | Roof Level | D3 | Zone D3 | 1383.41
Terminal 1 | Roof Level | D4 | Zone D4 | 484.55
Terminal 1 | Roof Level | E1 | Zone E1 | 1431.54
Terminal 1 | Roof Level | E2 | Zone E2 | 1697.69
Terminal 1 | Roof Level | E3 | Zone E3 | 1149.15
Terminal 1 | Roof Level | E4 | Zone E4 | 1575.71
Terminal 1 | Roof Level | F1 | Zone F1 | 1700.03
Terminal 1 | Roof Level | F2 | Zone F2 | 1428.08
Terminal 1 | Roof Level | F3 | Zone F3 | 1575.04
Terminal 1 | Roof Level | F4 | Zone F4 | 1186.65
Terminal 2 | Basement | E1 | Zone E1 | 260.66
Terminal 2 | Basement | E2 | Zone E2 | 647.47
Terminal 2 | Basement | E3 | Zone E3 | 263.84
Terminal 2 | Basement | E4 | Zone E4 | 697.8
Terminal 2 | Apron | A2 | Zone A2 | 252.32
Terminal 2 | Apron | A2 | Zone A2 | 297.97
Terminal 2 | Apron | A3 | Zone A3 | 474.94
Terminal 2 | Apron | A4 | Zone A4 | 953.09
Terminal 2 | Apron | A4 | Zone A4 | 486.68
Terminal 2 | Apron | B1 | Zone B1 | 296.25
Terminal 2 | Apron | B1 | Zone B1 | 293.46
Terminal 2 | Apron | B3 | Zone B3 | 1000.31
Terminal 2 | Apron | B3 | Zone B3 | 509.65
Terminal 2 | Apron | C1 | Zone C1 | 518.69
Terminal 2 | Apron | C2 | Zone C2 | 1384.87
Terminal 2 | Apron | C3 | Zone C3 | 712.12
Terminal 2 | Apron | C4 | Zone C4 | 1383.23
Terminal 2 | Apron | D1 | Zone D1 | 1420.77
Terminal 2 | Apron | D3 | Zone D3 | 1417.29
Terminal 2 | Apron | E1 | Zone E1 | 260.66
Terminal 2 | Apron | E2 | Zone E2 | 647.47
Terminal 2 | Apron | E3 | Zone E3 | 263.84
Terminal 2 | Apron | E4 | Zone E4 | 697.8
Terminal 2 | Apron | F1 | Zone F1 | 1502.34
Terminal 2 | Apron | F2 | Zone F2 | 1464.13
Terminal 2 | Apron | F4 | Zone F4 | 245.69
Terminal 2 | Apron | F4 | Zone F4 | 244.54
Terminal 2 | Apron | G1 | Zone G1 | 1591.09
Terminal 2 | Apron | G2 | Zone G2 | 1594.09
Terminal 2 | Apron | G3 | Zone G3 | 260.88
Terminal 2 | Apron | G3 | Zone G3 | 275.92
Terminal 2 | Apron | H1 | Zone H1 | 1128.22
Terminal 2 | Apron | H2 | Zone H2 | 1130.82
Terminal 2 | Apron | I1 | Zone I1 | 756.73
Terminal 2 | Apron | K1 | Zone K1 | 307.86
Terminal 2 | Apron | K1 | Zone K1 | 309.29
Terminal 2 | Apron | K3 | Zone K3 | 970.5
Terminal 2 | Arrival | A2 | Zone A2 | 416.78
Terminal 2 | Arrival | A4 | Zone A4 | 1092.48
Terminal 2 | Arrival | B1 | Zone B1 | 473.78
Terminal 2 | Arrival | B3 | Zone B3 | 1117.83
Terminal 2 | Arrival | C2 | Zone C2 | 1396.36
Terminal 2 | Arrival | C4 | Zone C4 | 1394.98
Terminal 2 | Arrival | D1 | Zone D1 | 1402.74
Terminal 2 | Arrival | D3 | Zone D3 | 1385.13
Terminal 2 | Arrival | E1 | Zone E1 | 236.68
Terminal 2 | Arrival | E2 | Zone E2 | 538.88
Terminal 2 | Arrival | E3 | Zone E3 | 263
Terminal 2 | Arrival | E4 | Zone E4 | 618.73
Terminal 2 | Arrival | F1 | Zone F1 | 1445.4
Terminal 2 | Arrival | F2 | Zone F2 | 1463.59
Terminal 2 | Arrival | F3 | Zone F3 | 266.61
Terminal 2 | Arrival | F4 | Zone F4 | 1383.7
Terminal 2 | Arrival | G1 | Zone G1 | 1668.32
Terminal 2 | Arrival | G2 | Zone G2 | 1480.83
Terminal 2 | Arrival | G3 | Zone G3 | 1612.18
Terminal 2 | Arrival | H1 | Zone H1 | 1063.65
Terminal 2 | Arrival | H2 | Zone H2 | 1089.45
Terminal 2 | Arrival | I1 | Zone I1 | 727.96
Terminal 2 | Arrival | K1 | Zone K1 | 1153.09
Terminal 2 | Arrival | K3 | Zone K3 | 995.26
Terminal 2 | Departure | A2 | Zone A2 | 409.62
Terminal 2 | Departure | A4 | Zone A4 | 1116.34
Terminal 2 | Departure | B1 | Zone B1 | 455.62
Terminal 2 | Departure | B3 | Zone B3 | 1194.48
Terminal 2 | Departure | C2 | Zone C2 | 1374.41
Terminal 2 | Departure | C4 | Zone C4 | 1409.6
Terminal 2 | Departure | D1 | Zone D1 | 1391.84
Terminal 2 | Departure | D3 | Zone D3 | 1393.01
Terminal 2 | Departure | E1 | Zone E1 | 232.62
Terminal 2 | Departure | E2 | Zone E2 | 608.56
Terminal 2 | Departure | E3 | Zone E3 | 261.19
Terminal 2 | Departure | E4 | Zone E4 | 667.72
Terminal 2 | Departure | F1 | Zone F1 | 1510.96
Terminal 2 | Departure | F2 | Zone F2 | 1431.02
Terminal 2 | Departure | F4 | Zone F4 | 1641.36
Terminal 2 | Departure | G1 | Zone G1 | 1556.69
Terminal 2 | Departure | G2 | Zone G2 | 1347.9
Terminal 2 | Departure | G3 | Zone G3 | 1677.45
Terminal 2 | Departure | H1 | Zone H1 | 1372.29
Terminal 2 | Departure | H2 | Zone H2 | 1104.62
Terminal 2 | Departure | I1 | Zone I1 | 758.15
Terminal 2 | Departure | K1 | Zone K1 | 1091.98
Terminal 2 | Departure | K3 | Zone K3 | 1084
Terminal 2 | Roof Level | A2 | Zone A2 | 409.62
Terminal 2 | Roof Level | A4 | Zone A4 | 1116.34
Terminal 2 | Roof Level | B1 | Zone B1 | 455.62
Terminal 2 | Roof Level | B3 | Zone B3 | 1194.48
Terminal 2 | Roof Level | C2 | Zone C2 | 1374.41
Terminal 2 | Roof Level | C4 | Zone C4 | 1409.6
Terminal 2 | Roof Level | D1 | Zone D1 | 1391.84
Terminal 2 | Roof Level | D3 | Zone D3 | 1393.01
Terminal 2 | Roof Level | E1 | Zone E1 | 232.62
Terminal 2 | Roof Level | E2 | Zone E2 | 608.56
Terminal 2 | Roof Level | E3 | Zone E3 | 261.19
Terminal 2 | Roof Level | E4 | Zone E4 | 667.72
Terminal 2 | Roof Level | F1 | Zone F1 | 1510.96
Terminal 2 | Roof Level | F2 | Zone F2 | 1431.02
Terminal 2 | Roof Level | F4 | Zone F4 | 1641.36
Terminal 2 | Roof Level | G1 | Zone G1 | 1556.69
Terminal 2 | Roof Level | G2 | Zone G2 | 1347.9
Terminal 2 | Roof Level | G3 | Zone G3 | 1677.45
Terminal 2 | Roof Level | H1 | Zone H1 | 1372.29
Terminal 2 | Roof Level | H2 | Zone H2 | 1104.62
Terminal 2 | Roof Level | I1 | Zone I1 | 758.15
Terminal 2 | Roof Level | K1 | Zone K1 | 1091.98
Terminal 2 | Roof Level | K3 | Zone K3 | 1084
Airside | Outside Terminal |  | AP111 | 10800
Airside | Outside Terminal |  | AP112 | 10800
Airside | Outside Terminal |  | AP113 | 8100
Airside | Outside Terminal |  | AP114 | 8100
Airside | Outside Terminal |  | AP115 | 8100
Airside | Outside Terminal |  | AP116 | 8100
Airside | Outside Terminal |  | AP117 | 8100
Airside | Outside Terminal |  | AP118 | 8100
Airside | Outside Terminal |  | AP119 | 8100
Airside | Outside Terminal |  | AP120 | 8100
Airside | Outside Terminal |  | AP121 | 8100
Airside | Outside Terminal |  | AP122 | 8100
Airside | Outside Terminal |  | AP123 | 13500
Airside | Outside Terminal |  | AP124 | 13500
Airside | Outside Terminal |  | AP211 | 8100
Airside | Outside Terminal |  | AP212 | 8100
Airside | Outside Terminal |  | AP213 | 8100
Airside | Outside Terminal |  | AP214 | 8100
Airside | Outside Terminal |  | AP215 | 8100
Airside | Outside Terminal |  | AP216 | 8100
Airside | Outside Terminal |  | AP217 | 8100
Airside | Outside Terminal |  | AP218 | 8100
Airside | Outside Terminal |  | AP219 | 8100
Airside | Outside Terminal |  | AP220 | 8100
Airside | Outside Terminal |  | AP221 | 8100
Airside | Outside Terminal |  | AP222 | 8100
Landside | Outside Terminal |  | R1001 | 1210
Landside | Outside Terminal |  | R1002 | 4960
Landside | Outside Terminal |  | R1003 | 3555
Landside | Outside Terminal |  | R1004 | 900
Landside | Outside Terminal |  | R1005 | 4230
Landside | Outside Terminal |  | R1006 | 1065
Landside | Outside Terminal |  | R1007 | 2460
Landside | Outside Terminal |  | R1008 | 4410
Landside | Outside Terminal |  | R1009 | 1230
Landside | Outside Terminal |  | R1010 | 1640
Landside | Outside Terminal |  | R1011 | 1110
Landside | Outside Terminal |  | R1012 | 840
Landside | Outside Terminal |  | R1013 | 350
Landside | Outside Terminal |  | R1014 | 880
Landside | Outside Terminal |  | P101 | 810
Landside | Outside Terminal |  | P102 | 810
Landside | Outside Terminal |  | P103 | 810
Landside | Outside Terminal |  | P104 | 810
Landside | Outside Terminal |  | P105 | 810
Landside | Outside Terminal |  | P106 | 810
Landside | Outside Terminal |  | P107 | 810
Landside | Outside Terminal |  | P108 | 810
Landside | Outside Terminal |  | P109 | 810
Landside | Outside Terminal |  | P110 | 810
Landside | Outside Terminal |  | P111 | 810
Landside | Outside Terminal |  | P112 | 810
Landside | Outside Terminal |  | P113 | 810
Landside | Outside Terminal |  | P114 | 810
Landside | Outside Terminal |  | P115 | 810
Landside | Outside Terminal |  | P116 | 810
Landside | Outside Terminal |  | P117 | 810
Landside | Outside Terminal |  | P118 | 810
Landside | Outside Terminal |  | P119 | 810
Landside | Outside Terminal |  | P120 | 810
Landside | Outside Terminal |  | P121 | 810
Landside | Outside Terminal |  | P122 | 810
Landside | Outside Terminal |  | P123 | 810
Landside | Outside Terminal |  | P124 | 810
Landside | Outside Terminal |  | T101 | 395
Landside | Outside Terminal |  | T102 | 395
Landside | Outside Terminal |  | T103 | 395
Landside | Outside Terminal |  | T104 | 395
Landside | Outside Terminal |  | T105 | 395
Landside | Outside Terminal |  | T106 | 395
Landside | Outside Terminal |  | T107 | 395
Landside | Outside Terminal |  | T108 | 395
Landside | Outside Terminal |  | T109 | 395
Landside | Outside Terminal |  | T110 | 395
Landside | Outside Terminal |  | T111 | 395
Landside | Outside Terminal |  | T112 | 395
Landside | Outside Terminal |  | T113 | 395
Landside | Outside Terminal |  | T114 | 395
Landside | Outside Terminal |  | T115 | 395
Landside | Outside Terminal |  | T116 | 395
Landside | Outside Terminal |  | T117 | 395
Landside | Outside Terminal |  | T118 | 395
Landside | Outside Terminal |  | T119 | 395
Landside | Outside Terminal |  | T120 | 395
Landside | Outside Terminal |  | T121 | 395
Landside | Outside Terminal |  | T122 | 395
Landside | Outside Terminal |  | T123 | 395
Landside | Outside Terminal |  | T124 | 395
Landside | Outside Terminal |  | T125 | 395
Landside | Outside Terminal |  | T126 | 395
Landside | Outside Terminal |  | T127 | 395
Landside | Outside Terminal |  | T128 | 395
Landside | Outside Terminal |  | T129 | 395
Landside | Outside Terminal |  | T130 | 395
Landside | Outside Terminal |  | T131 | 395
Landside | Outside Terminal |  | T132 | 395
Landside | Outside Terminal |  | T133 | 395
Landside | Outside Terminal |  | T134 | 395
Landside | Outside Terminal |  | T135 | 395
Landside | Outside Terminal |  | T136 | 395

## Facilities
General
Generator Room
Substation Room
Utility Building
Pump Room
Corridor
UPS Room
Pump Room
Passageway
Vestibule
Baggage Handling Area
Check-in Hall
Electrical Room
Gas Suppression Room
Primary IT Core
IT Room
ISP Room
Electrical Meter Cabinet
Fuel Tank Room
Chiller Plant Room
Lobby
AHU Plant
LV Switch Room
BHS Plant Deck
TX Substation and LV Switchroom
Foul Water Treatment Plant
Elec/Mech Room
Cooling Tower Space
Roofdeck

## Discipline
Disciplines
Architectural
Structural
Geotechnical
Mechanical
Electrical
Safety
Civil
Legal
Financial
Plumbing
FFP
Environment
Factory
General
O&M
Fitout
Permits
Testing
Fitout
IT

## CS
CS | Description | Mechanical Evaluation
0 | Not existing
1 | Very Good
2 | Good | The internal and external components does not have any major damage or wear, clean and free of excessive dust, dirt, and lubricants
3 | Fair | Theinternal and external components of the equipment have minor signs of damage or deteriorating wear and contain amounts of leaks, dirt and debris.
4 | Poor | The internal and external and internal components of the equipment shows major damage and significant deterioration and contains notable amounts of leaks, grease, lubricant, and debris
5 | Very Poor

## IS
IS | Definition
1 | Do Nothing
2 | Minor Repair
3 | Major Repair
4 | Rehabilitation
5 | Replacement
6 | Alternative Renewal
7 | Audit and Testing
8 | End of Life Service

## Others
Risk | Name |  | Score | Condition | Score | Serviceability | Score | Health Index
1 | Green |  | 1 | New or as new | 1 | Appropriate for use with >15 years spare capacity | 1 | Just built - monitor performance to design
2 | Amber |  | 2 | Good condition | 2 | Appropriate for use with >10 years spare capacity | 2 | >10 year planning period
3 | Red |  | 3 | Shows moderate sign of wear | 3 | Appropriate for use with >5 years spare capacity | 3 | Monitor - On the radar within 10 year horizon
|  |  | 4 | Intervention in next planning period | 4 | Fully utilised requiring investment in next planning period | 4 | Plan & close monitor - Next 5 year planning period
|  |  | 5 | Intervention this planning period | 5 | Needs urgent mitigation to address service issues | 5 | Action now - This planning period
Investigation Period
25 | years
Code Compliance
NC
C
CR
FV
Discount factor
0%
unit
m2
each
set
lot
m3 | [5 empty] | 720000000
m
Chi phi O&M cho nha xuong
64583.4903 | VND/m2/year
1.5 | 1
1.5 | 0.092903 | 6000
| 1 | 64583.4903
5381.9575

## Code
Design Code | Descipline | Name in English (Brief)
Philippine Green Building Code | Environment | Philippine Green Building Code
PEC 2009 | Electrical | Philippine Electrical code 2009
PEC 2017 | Environment | Philippine Electrical code 2017
NSCP 2010 | Structural | National Structural Code of the Philippines 2010 6th Edition
NSCP 2015 | Structural | National Structural Code of the Philippines 2015 7th Edition
ACI 224R-01 | Structural | American Concrete Institute 224R-1
NSCP 2010 | Structural
NSCP 2015 | Structural
ACI 360R-06 | Structural
Eurocode 2 | Structural
ACI 318-95 | Structural
DPWH bluebook | Civil
Philippine Mechanical Engineering Code 2012 | Mechanical
ASME A17.1 | Mechanical
OSHC Standard
RIRR (2019) of R.A. 9514 | Fire Fighting and Protection | Revised Implementing Rules and Regulations of R.A. 9514
IRR (2009) of R.A. 9514 | Fire Fighting and Protection | Implementing Rules and Regulations of R.A. 9514
NFPA 25 - 2011 | Fire Fighting and Protection
NFPA 25 - 2020 | Fire Fighting and Protection
565S2019 |  | LLDA BR No. 565 S. 2019/LISP Internal Memo
PD1096 | Architectural | National Building Code of the Philippines PD1096
RA9504 | General | xx
DesignDocs
JISR3208 | Architectural | Japanese Industrial Standards
JIS K5621 | Architectural | Japanese Industrial Standards
PD1185 | Fire Fighting and Protection | Fire Code of the Philippines
JIS A5207 | Plumbing | Japanese Industrial Standards
BP344 | Architectural | Accessibility Law
PGBC | Architectural | Philippine Green Building Code
IRR of R.A. 11058 | Fire Fighting and Protection | Implementing Rules and Regulations of R.A. 11058
PMEC2012 | Mechanical | Philippine Mechanical Engineering Code 2012

## NCR
Component | Items | Facility | Discipline | S | R | Design | C1 | Current | C2

## Description
Structural Component | Quantity | Unit | Charateristics | Remarks
Building Type |  |  | Portal Steel Frame Structure
Foundation |  |  | Isolated Footing | 600-700mm thk
Moment Resisting Frame |  |  | Steel Columns and beams
Architectural/ Civil Component |  |  | Charateristics | Remarks
Roof |  |  | with insulation | 10mm thk- W-885 metal roof
interior Walls |  |  | Gypsum board surface
Façade |  |  | 100mm pre-cast
Ceiling |  |  | Acoustic and gypsum board
Finishing |  |  | Tiles, Resin floor coating, carpets, wall paints and wall papers
Pavement |  |  | Portland Cement Concrete Pavement | 200 mm thk pavement with 150mm thk Subbase and 150mm thk base course
MEPF Component | Quantity | Capacity/Load | Unit | Remarks
Chiller | 2 | 500 | TR
Air Cooling and Air Heating Unit | 1 | 232.2 | kw
Freight Elevator | 2 | 4000 / 2000 | kg | the 2000kg lift was under maintenance
Passenger Elevator | 2 | 1000 / 500 | kg | used in office area
Transformer | 2 | 2500/ 500 | KVA | 1 Duty; 1 Stand-by
GENSET | 1 | 500 | KVA | No back up generator available
Lighting at Office |  |  | LUX
Lighting at Warehouse |  |  | LUX
Lighting Protection
CCTV |  |  | no.
Pumps | 1 | 1500 | GPM
Hydrants | 10
Tanks | 2 | 29720 | Gal | combined for domestic and fire fighting use
Booster Pumps | 3 | 3 | HP | 3 operational; no standby
Description | Component | Quantity | Capacity/Load | Unit | Brand | Warranty | Charateristics | Remarks
Structural
| Building Type | [5 empty] | Portal Steel Frame Structure
| Foundation | 475 |  | no. |  |  | Isolated Footing; 600-700mm thk
| Moment Resisting Frame | 44 |  | no. |  |  | Structural Steel Columns and beams
Architectural
| Façade | [5 empty] | - Common: 150mm Thk. Reinforced EVG-3D Wall Composed of 76mm thk. Polysterene - Entrance Façade: 8mm thk Tempered Clear Glass Façade
| Windows | [5 empty] | -Fixed Glass Window Panel - Aluminum Frame with powder coated finish
| Interior Walls | [5 empty] | Dry wall interior Partition
| Ceiling | [5 empty] | For offices: Acoustics and gypsum board
| Finishing | [5 empty] | Tiles, Resin floor coating, carpets, wall paints and wall papers
Civil
| Roads | 200 mm thk |  |  |  |  | 200mm PCCP with 150mm thk compacted base course
| Drainage | [5 empty] | Drainage: 460mm to 1050mm diameter RCP Canal: 600mmx1000mm with Steel grating Cover
Mechanical
| HVAC | [5 empty] | 2 Tower Chillers with 500 TR capacity; serves the building through FCU ( Floor Mounted, Ceiling Mounted)
| Freight Elevator | 2 | 4000 / 2000 | kg |  |  | 1 - 4000kg capacity 1 - 2000kg capacity
| Passenger Elevator | 2 | 1000 / 500 | kg |  |  | 1 - 1000kg capacity 1- 500kg capacity
Electricial
| Transformer | 2 | 2500/ 500 | KVA |  | Expired | 1 - 2.5 MVA 1 - 500KVA | 1 Duty; 1 Stand-by
| GENSET | 1 | 500 | KVA |  |  | 1 - 500KVA | No back up generator available
| Lighting Fixtures |  |  | LUX |  |  | No info on LUX level All lightings are LED
| Lighting Protection | [5 empty] | 3 lightning Arrester with 100m radius
| CCTV |  |  | no. |  |  | Building is equipped with CCTV; 360 degree and fixted type camera
| BMS | [5 empty] | No BMS installed
Fire Pro and FDAS
| Pumps | 1 | 1500 | GPM |  |  | 1 - 1500 GPM pump
| Hydrants | 10 |  |  |  |  | outdoor hydrants FHC inside the building No Fire sprinklers
| FDAS | [5 empty] | Fully Addressable System: Switch, Strobe lights and Horns, Smoke Detector, Manual Pull Station interconnected to Fire Alarm Control Panel
| Public Address | [5 empty] | Equipped - Located at the ground Floor Level
| Tanks | 2 | 29720 | Gal |  |  | 2 - 110 m3 tank | combined for domestic and fire fighting use
Hydraulics
| Booster Pumps | 3 | 3 | HP |  |  | 3 HP booster pumps | 3 operational; no standby
38

## Fitoutopion
Option | FitoutCost(Peso)
m2 | Min | Max
50000 | 8053 | 10233
40000 | 8678 | 10884
30000 | 9303 | 11535
20000 | 9927 | 12186
10000 | 10552 | 12837
5000 | 13676 | 16091

## Compiled
No |  |  |  | Items | Component | Findings | Floor | Facility | Discipline | YearBuilt | S | R | Design | C1 | Current | C2 | Interventions | Quantity | Unit | IS | InterPer | Cost | Span | Probability | Year | Binary_highrisk |  | NPV |  | NPV |  | NPV |  | NPV |  | NPV |  | NPV |  | NPV |  | NPV |  | NPV |  | NPV |  | NPV |  | NPV
No. |  | Categories |  | Items | Component | Findings | Floor | Facility | Discipline | YearBuilt | S | R | Design | Comply? | Current | C2 | Interventions | Quant. | Unit | IS | Inter Per | Cost |  | Prob | Year |  |  | Base | [7 empty] | Sensitivity Analysis 1 (without O&M) | [7 empty] | Sensitivity Analysis 2 (without O&M and Near Future Fitout)
[28 empty] | Conservative |  | Aggressive |  | Less Aggressive |  | Moderate |  | Conservative |  | Aggressive |  | Less Aggressive |  | Moderate |  | Conservative |  | Aggressive |  | Less Aggressive |  | Moderate
A |  | Against the law that impacts the permitting and operation | A | [24 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
RMG-EL-011 | 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | A
RMG-EL-012 | 2 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | A
B |  | Damage, Progressive Deterioration, Non-compliance that needs to be address Immediately | B | [24 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
LIC-AR-005 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
LIC-AR-012 | 1 |  | Consquence | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
LIC-AR-001 | 2 |  | Consquence | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
LIC-AR-018 | 3 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
LIC-AR-009 | 4 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
LIC-AR-007 | 5 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
Nam001 | 6 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
LIC-AR-015 | 7 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
LIC-AR-019 | 8 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
LIC-AR-008 | 9 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
LIC-AR-003 | 10 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
MRO-AR-02 | 11 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
OBV-AR-02 | 12 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
LIC-AR-014 | 13 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
OBV-AR-03 | 14 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
LIC-AR-016 | 15 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
OBV-AR-09 | 16 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
LIC-C-006 | 17 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
RMG-EL-005 | 18 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
RMG-EL-017 | 19 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
RMG-EL-008 | 20 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
RMG-EL-006 | 21 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
LIC-C-011 | 22 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
DDD-Fire-01 | 23 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
DDD-Fire-02 | 24 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
DDD-Fire-05 | 25 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
DDD-Fire-09 | 26 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
DDD-Fire-07 | 27 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
DDD-Fire-10 | 28 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
DDD-Fire-06 | 29 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
DDD-Fire-03 | 30 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
RAN-ME-005 | 31 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
RAN-ME-001 | 32 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
RAN-ME-013 | 33 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
RAN-ME-008 | 34 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
RAN-ME-006 | 35 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
RAN-ME-012 | 36 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
RAN-ME-012 | 37 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
RAN-ME-004 | 38 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
RAN-ME-007 | 39 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
RAN-ME-010 | 40 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
RAN-ME-014 | 41 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
LIC-P-001 | 42 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
CDO-HSE-03 | 43 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
CDO-HSE-04 | 44 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
LIC-ST-002 | 45 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
LIC-ST-004 | 46 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
LIC-ST-003 | 47 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
LIC-ST-001 | 48 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
RAN-ME-001a | 49 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
LIC-C-001a | 50 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | B
C |  | Best practice, damage can be observed but can be deferred, or agaisnt the law regulartion but not as strict | C | [24 empty] | 0 |  | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0 |  | 0 |  | 0 |  | 0 | 0 | 0
RMG-EL-013 | 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | C
OAT-ES-02 | 2 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | C
RMG-EL-009 | 3 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | C
CDO-HSE-05 | 4 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | C
LIC-C-010 | 5 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | C
LIC-C-004 | 6 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | C
LIC-AR-011 | 7 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | C
D |  | Optional Intervention | D | [24 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
LIC-AR-006 | 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | D
LIC-AR-002 | 3 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | D
LIC-AR-013 | 4 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | D
LIC-AR-010 | 5 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | D
E |  | At Risk Intervention (lack of documentation) | E | [24 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
OBV-AR-04 | 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E
RMG-EL-003 | 2 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E
LIC-C-001 | 3 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E
OAT-ES-03 | 4 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E
CDO-HSE-07 | 5 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E
RAN-ME-002 | 6 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E
RMG-EL-007 | 6 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E
RMG-EL-004 | 7 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | E
F |  | Future Intervention | F | [24 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
N001 | 1 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F
N006 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | C
N007 | 2 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F
N008 | 3 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F
N009 | 4 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F
N010 | 5 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F
N011 | 6 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F
N012 | 7 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F
N013 | 8 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F
N014 | 9 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F
N015 | 10 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F
N016 | 11 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | F
|  | Summary | [25 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
[28 empty] | A+B+C+D+E+F |  | A+B+C+D+F |  | A+B+C+F |  | A+B+F |  | A+B+C+D+E |  | A+B+C+D |  | A+B+C |  | A+B |  | A+B+C+D+E |  | A+B+C+D |  | A+B+C |  | A+B
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51

## print
No. | Categories | Base |  |  |  | Sensitivity Analysis 1 (without O&M) |  |  |  | Sensitivity Analysis 2 (without O&M and Near Future Fitout)
|  | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4 | 1 | 2 | 3 | 4
A | Against the law that impacts the permitting and operation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
B | Damage, Progressive Deterioration, Non-compliance that needs to be address Immediately | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
C | Best practice, damage can be observed but can be deferred, or agaisnt the law regulartion but not as strict | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
D | Optional Intervention | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E | At Risk Intervention (lack of documentation) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
F | Future Intervention | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Summary | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## doc1
No. | Documents | Status | Comment | Remarks | Confirmation from Owner
A | Documents on QC/QC and Operations
1 | List of design changes during construction, approvals and certifications from relevant authorities | NA |  | No records found or submited | Closed as confirmed there is no existence of the documents
2 | As-built drawings | A
3 | QA/QC report and plan | NA |  | No records found or submitted | No Available
4 | Specs of materials issued by manufacturers and suppliers and certifications of origins with approval of relevant governmental bodies | NA |  | Only general information on as-built drawings but no detailed specs provided by the suppliers/manufactuers.
5 | Conditional surveys and testing results during construction and operation | NA |  | No records found or submitted | Pavement test results
6 | Certified construction progress (e.g. quantity of work packages) | A
7 | Testing results done by third party if available for critical items (e.g. test pile) | NA |  | Critical tests are: (1) soil compaction; (2) fire resistance for steel structure; (3) concrete grade
8 | Installation schedule for equipment | A
9 | Operation Manuals | A |  | Only in hardcopy
10 | Agreement/certification issued from relevant bodies for the followings | A
10.1 | Fire fighting and protection certification | A | Incomplete | No fire resistance for steel structure done by police
10.2 | HSE | A
10.3 | Safety manuals for operations of assets and equipment | A
10.4 | Construction permit (if applicable) | A
10.5 | Approval on connections (e.g. infrastructure and shared utilities and services) | A | Incomplete | Misssing certificate of connection to electricity
11 | Defects and incident reports during construction (if available) and operations | A |  | only Post Earthquake Assessment Report found
12 | Handover certification | NA |  | No records found or submitted
13 | Certification from authorized bodies on the completion | A
B | Documents on Tenant's agreements
1 | Lease agreements and responsibility on maintenances | A |  |  |  | Did not provide lease agreement with other tenants
2 | Tenant's Operation Manuals (if applicable) | A
C | Documents for Design Review
1 | Design narrative that describes design criteria, capacity requirements, functions, governing codes and standards | NA |  | No records found or submitted
2 | Design calculation reports (with modelling approach) | NA |  | No records found or submitted
3 | Relevant reports for design such as geotechnical investigation, flood study, topographical map, environmental report. | A | Incomplete | Only geotechical report submitted
4 | Design drawings | A | Incomplete | No received mechanical drawings. Incomplete set of Architechtrual, Structural and Civil drawings
5 | Specs for components and materials | NA |  | No records found or submitted
6 | Bill of quantity and Fee estimate | NA |  | No records found or submitted
7 | Design review reports certified by relevant bodies | NA |  | No records found or submitted
Notes:
NA : Not Available
A : Available

## doc2
Technical Due Diligence of Aruze Gaming
for Altus Capital Partners
Request for Information for Due Diligence Study
As of | 2022-03-15
| General Information | Priority | Status | Comment | Review | Remarks | Questions
1.1 | Property description and particulars | Low
| Maximum Permissible and consumed GFAs | Low | A |  | Yes
| year of construction, year of last renovation works | Low | NA
| number of car park spaces | Low | NA
| details of any external areas etc | Low | A |  | Yes
1.2 | List of Consultants and Contractors Engaged and Copies of their respective Contracts ( Architect, Structural Engineer, Structural Engineer, Structural Engineer, Electrical Engineer, Quantity Surveyor, Sustainability Consultant, Sustainability Consultant, Roof Specialist, Other Consultants and Contractors ) | Low | PA |  | Yes | Availble: Designer, main contractors
1.3 | Building Insurance | High | A |  | Yes
1.4 | Details of any warranties or guarantees for the property
| Waterproofing | High | A |  | Yes | Still valid until 2026
| Architectural Finishes | High
| Cladding Systems | High
| Electrical and Auxillary | High
| Pumps | High
| Transformers | High
| Genset | High | A |  | yes | Expired
| Elevator Units | High
| HVAC | High | A |  | yes | Expired in Sep 2020
1.5 | Site history relating to any of the following (flooding, drainage issue, landslides, etc.) | Low | NA |  |  | Likely not important
1.6 | Historic Survey Reports | Medium | A |  | Yes | Geotech only
1.7 | Building Agreements
| State Lease Agreements | High | A |  | yes
| Supplemental State Lease | Low | NA |  | yes
| Easement Agreements | Low | A |  | yes
1.8 | Service Contracts
| HVAC | Medium | A |  | Yes
| Elevator maintenance | Medium | A |  | Yes
| Generator | Medium | A |  | Yes
| Roof Inspection/Cleaning | Low | A |  | Yes
| Janitorial Services | Low | A |  | Yes
| Security Services | Low | A |  | Yes
1.9 | Third-party vendor Reports
| Laboratory test reports | High | A |  | Yes
| Property Structural Condition Report | High | A |  | Yes | Post earthquake report
| Environmental Reports | High | A |  | yes
1.1 | Completion Certificate
| Architectural | High | NA
| Structural | High | NA
MEPF
| Transformers | High | A |  | yes
| Generator | High | A |  | yes
| Vertical transportation | High | A |  | yes
1.11 | Financial Documents ( Financial Reports, Tax Declaration, etc) | Low | A
2 | Statutory Approvals and Permits
2.1 | Occupancy Permits | High | A |  | yes
2.2 | Planning Permission | High | A |  | yes
2.3 | Certificate of Operation
| ELV | High | A |  | yes
| Genset | High | A |  | yes
2.4 | Environmental Certificates | High
| Certificate of Environmental Compliance | High | A |  | Yes
| Waste Generator Certificate | High | A |  | Yes
2.5 | Fire and Life Safety Permit | High | A |  | yes
2.6 | Sanitary Permit | High | A |  | Yes
2.7 | Electrical Certifications | High | A |  | Yes
2.8 | Connection to existing utilities
| sewerage and drainage | Medium | NA
| electricity | Medium | NA
| potable water | Medium | NA
2.9 | Statutory documentation including details of any planning restrictions, amendments, waivers or special conditions. | Medium | NA
2.1 | Any Environmental Audits that had been undertaken | High | A |  | yes
2.11 | Health & Safety audits, fire risk assessments etc to verify compliance with the latest Building Authority Regulations. | High | A |  | yes
2.13 | Other permits and Registration ( DOLE, CORTE, BIR, etc) | Low | A |  | yes
3 | Design & Specification
3.1 | As-Built Drawings
| Architectural | High | A |  | Yes | Copy from Design
| Structural | High | A |  | Yes | Copy from Design
| Mechanical | High | A |  | Yes | Copy from Design
| Electrical | High | A |  | Yes | Copy from Design
| Plumbing | High | A |  | Yes | Copy from Design
| Fire Protection | High | A |  | Yes | Copy from Design
| Façade | High | A |  | Yes | Copy from Design
| Auxilary | High | A |  | Yes | Copy from Design
| AVS | High | A |  | Yes | Copy from Design
| CATV | High | A |  | Yes | Copy from Design
| CCTV and AMS | High | A |  | Yes | Copy from Design
| DAS | High | A |  | Yes | Copy from Design
| FDAS | High | A |  | Yes | Copy from Design
| PABGM | High | A |  | Yes | Copy from Design
3.2 | Equipment and Load Schedule
| MEPF | High | A |  | Yes
3.3 | Design Drawings / Construction Drawings
| Architectural | High | A |  | Yes
| Structural | High | A |  | Yes
| Mechanical | High | A |  | Yes
| Electrical | High | A |  | Yes
| Plumbing | High | A |  | Yes
| Fire Protection | High | A |  | Yes
| Façade | High | A |  | Yes
| Auxilary | High | A |  | Yes
| AVS | High | A |  | Yes
| CATV | High | A |  | Yes
| CCTV and AMS | High | A |  | Yes
| DAS | High | A |  | Yes
| FDAS | High | A |  | Yes
| PABGM | High | A |  | Yes
3.4 | Structural design calculation | High | NA
3.5 | MEPF Schematic Design and Concept Design Report | High | NA
3.6 | Architectural and MEPF specification
| Architectural Finishes | High | NA
| MEPF materials and systems specs | High | NA
3.7 | Basis of Design Report
| Structural | High | NA
| MEPF | High | NA
| Lighting Design | High | NA
3.8 | Single Line Diagrams for building M&E Services. | High | A |  | Yes
3.9 | Drawings for LV System -
| Transformers | High | A |  | Yes
| Generator | High | A |  | Yes
| LV Switchboards | High | A |  | Yes
| MCBs | High | A |  | Yes
| lighting and small power | High | A |  | Yes
3.1 | MEPF and Buidling Equipment Schedule | High | A |  | Yes
3.11 | All building equipment operation manual | High | A |  | Yes
3.12 | Geotechnical Report
| Soil Investigation Report | High | A |  | Yes
3.13 | QA/QC or any report -for Fire Resistivity of Structural Steel paint, compaction value of internal roads | High | NA |  | Yes
4 | Testing & Commissioning, Maintenance and Inspection Records
4.1 | All MEPF T&C Test Data/Reports (HVAC, ELV, etc) | High | A |  | Yes
4.2 | All PMS and Service Records that pertain to MEPF system. | High | A |  | Yes
4.3 | Maintenance records
| ELV System | High | A |  | Yes
| BMS | High | A |  | Yes
| CCTV | High | A |  | Yes
| Access Control | High | A |  | Yes
| Public Address | High | A |  | Yes
4.4 | Maintenance records for LV System
| (Transformers | High | A |  | Yes
| Generator | High | A |  | Yes
| LV Switchboards | High | A |  | Yes
| MCBs | High | A |  | Yes
| lighting and small power | High | A |  | Yes
4.5 | Vertical transportation (elevators) maintenance records | High | A |  | Yes
6 | Property Information
6.1 | Asset List | Medium | NA
| Long lead items | Medium | NA
6.2 | Copy of Certificates for authority recognition of quality water, quality air, energy efficiency. | High | NA
| Air Emissions | Low | NA
| Exhaust | Medium | NA
6.3 | Structural Integrity Certification or any existing Structural Assessment Reports undertaken | High | A |  |  | Post earthquake
6.4 | Permit to Operate Records | High | A |  | Yes
7 | Other related information
7.1 | Hazardous Materials inventory | High | A |  | Yes
7.2 | Standard operating procedure for Fire and Life Safety, Health and Safety Proedures, Natural Calamities - Earthquakes, typhoons, volcanic eruptions and the likes,and Security informations including terrorist attacks, etc. | High | A |  | Yes
7.3 | History of Repairs | Medium | NA
7.4 | Asset warehouse inventory | Medium | NA
7.5 | Corporate Documents of Seller ( General Information sheet, IRT and AFS, SEC Registration, Certificate of Incorporation, Memorandum and Articles ofAssociation, Certificate of Good Standing) | Low | NA

## questions
No | Questions | Do you have it? | Note from Asure on answers
1 | Fire resistance paint certification for steel structure issued by police station
2 | Design calculation for pavement |  |  | yes
3 | Design calculation for concrete slab |  |  | no
4 | Design calculation for MEPF
5 | Design service life
6 | recent 12 month repair plan
7 | future 12 month repair plan
8 | Specification of epoxy paint used for all floors of warehouse areas
9 | Structural repair/restrengthening per recommendation from post earthquake report
10 | Report/certificate produced by the Bureau of Fire protection
11 | Value of E-modulus for base course of the pavement
12
13
14
15

## runway
No. | Segment | Condition | Serviceaility | Health Index | Size | Unit | Findings | Picture CODE
| 100 | 3 | 2 | 1 | 338 | m2 | Crack on segment | 100-01
101
102
103
104
105
106
107
108
109
110
111
112
113
114
115
116

## t1-floor
No. | Segment | Area | Zone | Facility | Discipline | Findings | Qty
1 | Door and window | 100-01
2 | Ceiling system
Floor finishing
Wall
Lighting
Smorking dectection system
Alarming system
Sprinkler
Emergency Signage
Door and window
Ceiling system
Floor finishing
Wall
Lighting
Smorking dectection system
Alarming system
Sprinkler
Emergency Signage

## A,C,S 1
Zone
Facility
No. | Item | Area | Discipline | Findings | % Qty
Door
Window
Façade

## t1-ceiling
No. | Segment | CS | Remarks | Picture CODE
| 100 | 3 |  | 100-01
| 101 | 5
| 102 | 2
103
104
105
106
107
108
109
110
111
112
113
114
115
116

## Electrical Equipment
No. | Equipment | QTY | Unit | Area | Facility | CS | Findings | Picture CODE
| MV Panel |  | no | Terminal 2 | General
| Transformers (confirm capacity) |  | no | Terminal 2 | General
| Low Voltage Switchboard |  | no | Terminal 2 | Apron
| Low Voltage Switchboard |  | no | Terminal 2 | Arrival
| Low Voltage Switchboard |  | no | Terminal 2 | Terminal Building
| Power Factor Correction (Capacitor Banks) |  | no | Terminal 2 | General
| Generator |  | no | Terminal 2 | General
| Fuel Tank |  | no | Terminal 2 | General
| Busducts / Busways |  | m2 | Terminal 2 | General
| Grounding System |  | m2 | Terminal 2 | General
| SCADA System |  | m2 | Terminal 2 | General
| Small Power |  | m2 | Terminal 2 | General
| Earthing and Lightning |  | m2 | Terminal 2 | General

## t1-Fire Pro
No. | Segment | Terminal | Phase | Level | Zone | Facility | Discipline | Findings | Qty
1 |  | Terminal 2 | Phase 1 | Apron Level | Zone 01 |  | Automatic sprinkler system | Lacking of sprinkler at corridor-like space adjacent to DIS WC; No sprinklers at corridor-like spaces near the comfort rooms; No sprinklers at the Electrical Room
2 |  | Terminal 2 | Phase 1 | Apron Level | Zone 04 |  | Automatic sprinkler system | No sprinklers at a room for future tenant space; No sprinklers at corridor-like spaces near the comfort rooms;
|  | Terminal 2 | Phase 1 | Apron Level | Zone 05 |  | Automatic sprinkler system | No sprinklers at the Generator RM, Electrical Meter Cabinet, Fuel Tank RM; No sprinklers at the corridor from BMS RM to stair case; No sprinkler at a room enclosing a column near the Staff WC
|  | Terminal 2 | Phase 1 | Apron Level | Zone 06 |  | Automatic sprinkler system | No sprinklers at the Electrical RM; LV Switch Room
|  | Terminal 2 | Phase 1 | Apron Level | Zone 07 |  | Automatic sprinkler system | No Sprinkler at the Electrical RM
|  | Terminal 2 | Phase 1 | Apron Level | Zone 08 |  | Automatic sprinkler system | No Sprinkler at the Electrical RM
|  | Terminal 2 | Phase 1 | Apron Level | Zone 09 |  | Automatic sprinkler system | No Sprinkler at the Electrical RM
|  | Terminal 2 | Phase 1 | Apron Level | Zone 10 |  | Automatic sprinkler system | No Sprinkler at the IT RM
|  | Terminal 2 | Phase 1 | Apron Level | Zone 11 |  | Automatic sprinkler system | No sprinklers at corridor-like spaces near the comfort rooms; No sprinklers at the Electrical Room
|  | Terminal 2 | Phase 1 | Arrival Level | Zone 01 |  | Automatic sprinkler system | No Sprinkler at the Electrical RM; Primary IT Core Room is under Gas Suppression System
|  | Terminal 2 | Phase 1 | Arrival Level | Zone 02 |  | Automatic sprinkler system | No Sprinkler at the Electrical RM; IT Room is under Gas Suppression System
|  | Terminal 2 | Phase 1 | Arrival Level | Zone 03 |  | Automatic sprinkler system | ISP RM is under Gas Suppression System
|  | Terminal 2 | Phase 1 | Arrival Level | Zone 05 |  | Automatic sprinkler system | No sprinkler at TX Substation and LV switchroom, UPS room, IT RM
|  | Terminal 2 | Phase 1 | Arrival Level | Zone 06 |  | Automatic sprinkler system | No sprinkler at Electrical RM, IT RM, and IT RM; No sprinklers at corridor-like spaces near the comfort rooms
|  | Terminal 2 | Phase 1 | Arrival Level | Zone 07 |  | Automatic sprinkler system | No sprinklers at corridor-like spaces near the comfort rooms; No sprinklers at the Electrical/Mechanical Room, IT RM; AOCC is under Gas Suppression System but some parts are under sprinkler; CRITICAL - no automatic protection for STO., Pantry and Manager RM
|  | Terminal 2 | Phase 1 | Arrival Level | Zone 08 |  | Automatic sprinkler system | No sprinklers at the IT RM
|  | Terminal 2 | Phase 1 | Arrival Level | Zone 09 |  | Automatic sprinkler system | No sprinklers at the Electrical/Mechanical Room
|  | Terminal 2 | Phase 1 | Arrival Level | Zone 10 |  | Automatic sprinkler system | No Sprinkler at the IT RM;
|  | Terminal 2 | Phase 1 | Arrival Level | Zone 11 |  | Automatic sprinkler system | No sprinkler at Electrical RM, and IT RM
|  | Terminal 2 | Phase 1 | Departure Level | Zone 01 |  | Automatic sprinkler system | No sprinkler but to be verified on site.
|  | Terminal 2 | Phase 1 | Departure Level | Zone 02 |  | Automatic sprinkler system | No sprinkler but to be verified on site.
|  | Terminal 2 | Phase 1 | Departure Level | Zone 03 |  | Automatic sprinkler system | No sprinkler but to be verified on site.
|  | Terminal 2 | Phase 1 | Departure Level | Zone 04 |  | Automatic sprinkler system | No sprinkler but to be verified on site.
|  | Terminal 2 | Phase 1 | Departure Level | Zone 04 |  | Automatic sprinkler system | No sprinkler but to be verified on site; No sprinklers at corridor-like spaces near the comfort rooms
|  | Terminal 2 | Phase 1 | Departure Level | Zone 05 |  | Automatic sprinkler system | No sprinkler but to be verified on site; No Sprinkler at the Electrical RM
|  | Terminal 2 | Phase 1 | Departure Level | Zone 06 |  | Automatic sprinkler system | No Sprinkler at the Electrical RM; No sprinklers at corridor-like spaces near the comfort rooms; Lacking sprinkler at the corridor beside the staircase; No sprinklers at the F&B Seating, retail
|  | Terminal 2 | Phase 1 | Departure Level | Zone 07 |  | Automatic sprinkler system | No sprinklers at Electrical/Mechanical RM; No sprinklers at F&B Seating, F&B Kitchen (critical), Access Corridor, IT Opening; No sprinklers at corridor-like spaces near the comfort rooms; Lacking sprinklers at retails
|  | Terminal 2 | Phase 1 | Departure Level | Zone 08 |  | Automatic sprinkler system | No sprinkler but to be verified on site; No Sprinkler at the Electrical RM; No sprinklers at corridor-like spaces near the comfort rooms
|  | Terminal 2 | Phase 1 | Departure Level | Zone 09 |  | Automatic sprinkler system | No sprinkler but to be verified on site.
|  | Terminal 2 | Phase 1 | Departure Level | Zone 11 |  | Automatic sprinkler system | No sprinkler but to be verified on site; No Sprinkler at the Electrical RM
|  | Terminal 2 | Phase 1 | Under Roof Level | Zone 01 |  | Automatic sprinkler system | No sprinkler but to be verified on site.
|  | Terminal 2 | Phase 1 | Under Roof Level | Zone 02 |  | Automatic sprinkler system | No sprinkler but to be verified on site.

## Opex-headcount
Year | head | cost
2017 | 249 | 208049176
2018 | 281 | 251077146
2019 | 283 | 311103689
2020 | 249 | 252963005
2021 | 187 | 228114045